## LDTA Flow
SampleDate | InFlow | EffFlow | ClarSludge | Rainfall | Weather | Odour | SplitterpH | SplitterDO | SplitterTemp | BPVol | Cells
2019-07-01 | 1410 | 1435 | / |  |  |  | 7.1 | 0.1 | 14.2 | 36 | 6/1
2019-07-02 | 1405 | 1400 | / |  |  |  | 7.1 | 0.2 | 14.7 | 39 | 1/2 | Flow to LDTA
2019-07-03 | 1405 | 1400 | / |  |  |  | 7.1 | 0.2 | 14.9 | 21 | 2/3 |  | Inflow (m3/d) | Outflow (m3/d) | Predicted Inflow 2035 (m3/d) | Maximum | Period
2019-07-04 | 1593 | 2156 | / |  |  |  | 7.1 | 0.2 | 14.9 | 33.5 | 3/4
2019-07-05 | 1542 | 1669 | / |  |  |  | 6.9 | 0.2 | 14.6 | 27.3 | 4/5 | Max | 4102 | 2836 |  | 2820 | 2020-07-01
2019-07-06 | 1609 | 1669 | / |  |  |  | / | / | / | / | 4 | Average | 1722.8904 | 1660.2011 | 2090 | 2820 | 2020-06-30
2019-07-07 | 1535 | 1563 | / |  |  |  | / | / | / | / | 4 | Median | 1617.5 | 1544
2019-07-08 | 1580 | 1506 | / |  |  |  | 7.1 | 0.1 | 14.5 | 44 | 4/5 | Min | 778 | 0
2019-07-09 | 1496 | 1506 | / |  |  |  | 6.9 | 0.1 | 14.4 | 24.1 | 5/6
2019-07-10 | 1439 | 1407 | / |  |  |  | 6.9 | 0.2 | 14.5 | 26 | 6/1
2019-07-11 |  |  | / |  |  |  | 6.9 | 0.2 | 14.7 | 36 | 1/2
2019-07-12 | 1652 | 1445 | /
2019-07-13 | 1605 | 1811 | / |  |  |  | / | / | / | / | 3
2019-07-14 | 2183 | 1811 | / |  |  |  | / | / | / | / | 3
2019-07-15 | 1927 | 2513 | / |  |  |  | 6.8 | 0.1 | 14.1 | / | 3/4
2019-07-16 | 1927 | 2513 | / |  |  |  | 6.9 | 0.1 | 14.5 | / | 4
2019-07-17 | 2548 | 2706 | / |  |  |  | 6.8 | 0.5 | 14.3 | 28.9 | 4/5
2019-07-18 | 2211 | 2706 | / |  |  |  | 7.1 | 0.2 | 14.5 | 30.4 | 5
2019-07-19 | 2023 | 2463 | / |  |  |  | 7 | 0.7 | 14.4 |  | 5/6
2019-07-20 | 2243 | 2554 | / |  |  |  | / | / | / |  | 6
2019-07-21 | 2891 | 2554 | / |  |  |  | / | / | / | / | 6
2019-07-22 | 2112 | 2801 | / |  |  |  | 6.8 | 0.2 | 14.4 | 38.7 | 6/1
2019-07-23 | 2167 | 2801 | / |  |  |  | 6.8 | 0.2 | 14 | / | 1
2019-07-24 | 2049 | 2358 | / |  |  |  | 7 | 3.3 | 13.5 |  | 1/2
2019-07-25 | 1913 | 2279 | / |  |  |  | 6.9 | 0.3 | 14.4 | 21.2 | 2
2019-07-26 | 2574 | 2090 | / |  |  |  | 7.1 | 0.2 | 14.9 | / | 2/3
2019-07-27 | 2453 | 1926 | / |  |  |  | / | / | / | / | 3
2019-07-28 | 1746 | 1759 | / |  |  |  | / | / | / | / | 3
2019-07-29 | 1658 | 1738 | / |  |  |  | 6.9 | 0.2 | 13.9 |  | 3/4
2019-07-30 | 1562 | 1767 | / |  |  |  | 7 | 0.2 | 11.1 |  | 4
2019-07-31 | 1856 | 1818 | / |  |  |  | 7.3 | 0.1 | 13.8 |  | 5
2019-08-02 | 1648 | 2004 | / |  |  |  | 7.3 | 1.1 | 13.5 |  | 5/6
2019-08-03 | 1713 | 1782 | / |  |  |  | / | / | / | / | 6
2019-08-04 | 1651 | 1668 | / |  |  |  | / | / | / | / | 6
2019-08-05 | 1613 | 1613 | / |  |  |  | 7.5 | 0.1 | 13.3 | / | 6/1
2019-08-06 | 1559 | 1485 | / |  |  |  | 7.5 | 0.2 | 13.6 | / | 1
2019-08-07 | 1510 | 1476 | / |  |  |  | 7.6 | 0.1 | 12.8 | / | 1/2
2019-08-08 | 1497 | 1522 | / |  |  |  | 7.3 | 0.1 | 14.3 | / | 2
2019-08-09 | 1785 | 1672 | / |  |  |  | 7.3 | 0.1 | 14.8 | / | 2/3
2019-08-10 | 1796 | 1751 | / |  |  |  | / | / | / | / | 3
2019-08-11 | 2433 | 2144 | / |  |  |  | / | / | / | / | 3
2019-08-12 | 4102 | 2764 | / |  |  |  | 7.1 | 0.5 | 14 | 36.7 | 3/4
2019-08-13 | 3262 | 2836 | / |  |  |  | 7.2 | 5.4 | 13.2 |  | 4
2019-08-14 | 2681 | 2803 | / |  |  |  | 7.4 | 3.4 | 13.8 | 26.8 | 4/5
2019-08-15 | 2332 | 2801 | / |  |  |  | 7.1 | 2.2 | 13.9 | 28.3 | 5
2019-08-16 | 2103 | 2802 | / |  |  |  | 7.1 | 0.8 | 14.2 | 27.2 | 5/6
2019-08-17 | 2234 | 2804 | / |  |  |  | / | / | / | / | 6
2019-08-18 | 2233 | 2803 | / |  |  |  | / | / | / | / | 6
2019-08-19 | 1967 | 2801 | / |  |  |  | 7.1 | 0.4 | 13.5 |  | 6/1
2019-08-20 | 1853 | 2435 | / |  |  |  | 7.1 | 0.3 | 9.2 | / | 1
2019-08-21 | 1869 | 2103 | / |  |  |  | 7.6 | 0.2 | 14.1 | / | 1/2
2019-08-22 | 2323 | 2181 | / |  |  |  | 7.1 | 0.3 | 14 | / | 2
2019-08-23 | 2341 | 2661 | / |  |  |  | 7.3 | 0.5 | 14.1 | / | 2/3
2019-08-24 | 2319 | 2509 | / |  |  |  | / | / | / | 22.1 | 3
2019-08-25 | 2125 | 2328 | / |  |  |  | / | / | / | 17.4 | 3
2019-08-26 | 1979 | 2132 | / |  |  |  | 7.1 | 0.4 | 14.5 | / | 3/4
2019-08-27 | 1911 | 2079 | / |  |  |  | 7.1 | 0.3 | 14.2 | 21.8 | 4
2019-08-28 | 1826 | 1920 | / |  |  |  | 7 | 0.4 | 14.4 | 30.2 | 4/5
2019-08-29 | 1709 | 1647 | / |  |  |  | 7.1 | 0.4 | 14.5 | 26.3 | 5
2019-08-30 | 1690 | 1694 | / |  |  |  | 7.1 | 0.1 | 14.8 | 28.6 | 5/6
2019-08-31 | 1711 | 1544 | / |  |  |  | 7.3 | 1 | 13.8 | / | 5
2019-09-01 | 1678 | 1544 | / |  |  |  | / | / | / | / | 6
2019-09-02 | 1547 | 1522 | / |  |  |  | 7.4 | 0.1 | 15.6 |  | 6/1
2019-09-03 | 1558 | 1525 | / |  |  |  | 7.6 | 0.2 | 14.9 | / | 1
2019-09-04 | 1474 | 1409 | / |  |  |  | 7.4 | 0.2 | 15.7 | / | 1/2
2019-09-05 | 1608 | 1462 | / |  |  |  | 7.5 | 0.1 | 14.2 | / | 2
2019-09-06 | 1797 | 1400 | / |  |  |  | 7.1 | 0.1 | 14.4 | / | 2/3
2019-09-07 | 1702 | 2140 | / |  |  |  | / | / | / | / | 3
2019-09-08 | 1602 | 1373 | / |  |  |  | / | / | / | / | 3
2019-09-09 | 1587 | 1904 | / |  |  |  | 7.1 | 0.1 | 14.3 | / | 3/4
2019-09-10 | 1544 | 1570 | / |  |  |  | 7.3 | 0.1 | 14.7 | / | 4
2019-09-11 | 1517 | 1449 | / |  |  |  | 7.1 | 0.2 | 14.8 | 23.5 | 4/5
2019-09-12 | 1474 | 1214 | / |  |  |  | 7.2 | 0.1 | 14.2 | 27.6 | 5
2019-09-13 | 1434 | 1196 | / |  |  |  | 7.3 | 0.1 | 12.2 |  | 5/6
2019-09-14 | 1606 | 1354 | /
2019-09-15 | 1722 | 1453 | / |  |  |  | / | / | / | / | 6
2019-09-16 | 1578 | 1167 | / |  |  |  | 7.4 | 0.2 | 14.8 | / | 6/1
2019-09-17 | 1531 | 1509 | / |  |  |  | / | / | / | / | 1
2019-09-18 | 1619 | 1351 | / |  |  |  | 7.3 | 0.2 | 15.2 | 30.9 | 1/2
2019-09-19 | 1563 | 1358 | / |  |  |  | 7.2 | 0.1 | 14.9 |  | 2
2019-09-20 | 1548 | 2071 | / |  |  |  | 7 | 0.2 | 15.6 |  | 2/3
2019-09-21 | 1595 | 1728 | / |  |  |  | / | / | / |  | 3
2019-09-22 | 1542 | 1561 | / |  |  |  | / | / | / | 20.7 | 3
2019-09-23 | 1441 | 1482 | / |  |  |  | 7.3 | 0.1 | 15.3 | 26.2 | 3/4
2019-09-24 | 1661 | 1711 | / |  |  |  | 7 | 0.1 | 15.2 |  | 4
2019-09-25 | 1643 | 1273 | / |  |  |  | 7.3 | 0.1 | 14 |  | 4/5
2019-09-26 | 1654 | 1304 | / |  |  |  | 7.2 | 2.4 | 13.4 |  | 5
2019-09-27 | 1561 | 1215 | / |  |  |  | 7.1 | 1.6 | 14.6 |  | 5
2019-09-28 | 1592 | 1320 | / |  |  |  | / | / | / | / | 5
2019-09-29 | 1500 | 1238 | / |  |  |  | / | / | / | / | 5
2019-09-30 | 1568 | 977 | / |  |  |  | 7.2 | 2.5 | 15.5 |  | 5/6
2019-10-01 | 1754 | 1504 | / |  |  |  | 7.1 | 2.2 | 14.6 | / | 6
2019-10-02 | 1683 | 1772 | / |  |  |  | 7.4 | 2.2 | 13.9 | / | 6
2019-10-03 | 1641 | 893 | / |  |  |  | 7.1 | 2.6 | 13.7 | / | 6
2019-10-04 | 1581 | 1819 | / |  |  |  | 7.2 | 3.8 | 13.2 | / | 6
2019-10-05 | 1671 | 2032 | / |  |  |  | / | / | / | / | 6
2019-10-06 | 1775 | 2426 | / |  |  |  | / | / | / | / | 6
2019-10-07 | 1640 | 1546 | / |  |  |  | 7 | 0.2 | 15.2 | / | 6/1
2019-10-08 | 1560 | 954 | / |  |  |  | 7.1 | 2.3 | 15.6 | 37.3 | 1
2019-10-09 | 1543 | 1514 | / |  |  |  | 7.2 | 0.8 | 15.2 | / | 1/2
2019-10-10 | 1515 | 1567 | / |  |  |  | 7 | 0.2 | 16.1 | / | 2
2019-10-11 | 2299 | 1202 | / |  |  |  | 7.3 | 2.1 | 16.2 | / | 2/3
2019-10-12 | 1827 | 2016 | / |  |  |  | / | / | / | / | 3
2019-10-13 | 1726 | 1938 | / |  |  |  | / | / | / | 12.9 | 3
2019-10-14 | 1639 | 1603 |  |  |  |  | 7.2 | 2.8 | 17.8 |  | 3/4
2019-10-15 | 1482 | 1617 | / |  |  |  | 7.2 | 2.3 | 16.9 |  | 4
2019-10-16 | 1375 | 1775 | / |  |  |  | 7.2 | 1.6 | 16.3 | / | 4/5
2019-10-17 | 1558 | 684 | / |  |  |  | 7.4 | 0.2 | 16.9 | / | 5
2019-10-18 | 1846 | 1321 | / |  |  |  | 7.2 | 1.7 | 17.2 | / | 5/6
2019-10-19 | 2932 | 2684 | / |  |  |  | / | / | / | 26.7 | 6
2019-10-20 | 2154 | 2447 | / |  |  |  | / | / | / | / | 6
2019-10-21 | 2154 | 2420 | / |  |  |  | 7.3 | 1.6 | 15.9 | / | 1/6
2019-10-22 | 2076 | 2595 | / |  |  |  | 7.5 | 2.2 | 15.7 | 22.9 | 1
2019-10-23 | 2218 | 2128 | / |  |  |  | 7 | 0.4 | 15.4 | / | 1/2
2019-10-24 | 1975 | 2275 | / |  |  |  | 7.1 | 2 | 15 | 27.5 | 2
2019-10-25 | 1984 | 1940 | / |  |  |  | 7.1 | 2.2 | 15.5 |  | 2/3
2019-10-26 | 1859 | 853 | / |  |  |  | / | / | / | / | 3
2019-10-27 | 1714 | 2538 | / |  |  |  | / | / | / | / | 3
2019-10-28 | 1943 | 1126 | / |  |  |  | 7.2 | 2.9 | 16.7 | 23 | 3
2019-10-29 | 1790 | 2486 | / |  |  |  | 7.3 | 2.4 | 17.3 |  | 3/4
2019-10-30 | 1723 | 774 | / |  |  |  | 7.2 | 3 | 16.7 | / | 4
2019-10-31 | 1668 | 1800 | / |  |  |  | 7.7 | 2.5 | 16.3 | 25 | 4
2019-11-01 | 1639 | 716 | / |  |  |  | 7.3 | 2.2 | 16.9 | / | 5
2019-11-02 | 1639 | 2400 | / |  |  |  | / | / | / | / | 5
2019-11-03 | 1657 | 2397 | / |  |  |  | / | / | / | / | 5
2019-11-04 | 1567 | 1495 | / |  |  |  | 7.3 | 2.5 | 18.3 | 38.3 | 5/6
2019-11-05 | 1488 | 625 | / |  |  |  | 7.3 | 2.4 | 18.5 | / | 6
2019-11-06 | 1495 | 2148 | / |  |  |  | 7.1 | 2.3 | 17.8 | / | 1/6
2019-11-07 | 1524 | 1761 | / |  |  |  | 7.2 | 0.2 | 17.9 | 20.8 | 1
2019-11-08 | 1449 | 1485 | / |  |  |  | 7.2 | 0.1 | 18.1 | / | 1/2
2019-11-09 | 1507 | 1332 | / |  |  |  | / | / | / | / | 2
2019-11-10 | 2003 | 1439 | / |  |  |  | / | / | / | 12.8 | 2
2019-11-11 | 2003 | 2119 | / |  |  |  | 7.1 | 0.8 | 17.2 | / | 2/3
2019-11-12 | 1802 | 707 | / |  |  |  | 7.5 | 1.5 | 17.7 | 25.2 | 3
2019-11-13 | 1667 | 2467 | / |  |  |  | 7.1 | 1.2 | 17.5 |  | 3/4
2019-11-14 | 1801 | 2467 | / |  |  |  | 7 | 0.1 | 18.5 |  | 4
2019-11-15 | 1969 | 2333 | / |  |  |  | 6.9 | 0.2 | 17.2 |  | 4/5
2019-11-16 | 1759 | 1959 | / |  |  |  | / | / | / | / | 5
2019-11-17 | 2264 | 1794 | / |  |  |  | / | / | / | / | 5
2019-11-18 | 2181 | 2330 | / |  |  |  | 7.2 | 0.1 | 16.7 | / | 5/6
2019-11-19 | 2157 | 1846 | / |  |  |  | 6.9 | 0.1 | 16.3 | 34.8 | 6
2019-11-20 | 2067 | 2245 | / |  |  |  | 7 | 0.2 | 16.2 | / | 6/1
2019-11-21 | 2058 | 2051 | / |  |  |  | 6.9 | 0.1 | 16.4 | 23.5 | 1
2019-11-22 | 1835 | 1855 | / |  |  |  | 6.9 | 0.4 | 17.2 |  | 1/2
2019-11-23 | 1852 | 1657 | / |  |  |  | / | / | / | / | /
2019-11-24 | 1711 | 1607 | / |  |  |  | / | / | / | / | /
2019-11-25 | 1747 | 1564 | / |  |  |  | 6.9 | 0.3 | 17.9 | 38.2 | 2/3
2019-11-26 | 1667 | 1535 | / |  |  |  | 6.9 | 0.2 | 18.6 | / | 3
2019-11-27 | 1625 | 1455 | / |  |  |  | 7.1 | 0.3 | 18.6 | / | 3/4
2019-11-28 | 1598 | 1397 | / |  |  |  | 7.2 | 0.3 | 19.4 | / | 4
2019-11-29 | 1563 | 1349 | / |  |  |  | 7.1 | 0.5 | 19.7 | / | 4/5
2019-11-30 | [6 empty] | 7 | 0.5 | 19.7 | / | 5
2019-12-01 | 1582 | 1228 | / | 0 | / | / | / | / | / |  | 5
2019-12-02 | 1507 | 1035 | 24 | 0 | overcast/warm | none | 7.3 | 0.3 | 19.1 | 13.4 | 5/6
2019-12-03 | 1768 | 1432 | 24 | 1 | wet | none | 7.5 | 0.1 | 18.8 | 35.8 | 6
2019-12-04 | 1642 | 1547 | 24 | 1 | overcast/fine | none | 7.1 | 0.2 | 18.4 | 24.7 | 6/1
2019-12-05 | 1592 | 1547 | 23 | 0 | overcast/fine | none | 7 | 0.2 | 18.8 | 25 | 1
2019-12-06 | 1612 | 1426 | / | 1 | Fine | none | 7 | 0.2 | 18.5 | / | 1/2
2019-12-07 | 1612 | 1358 | / | 1 | overcast | none | / | / | / | / | 2
2019-12-08 | 2270 | 1534 | / | 0 | rain | none | / | / | / | / | 2
2019-12-09 | 1879 | 2504 | 17 | 0 | Fine | none | 7 | 0.1 | 19.3 | 19 | 2/3
2019-12-10 | 1715 | 2023 | / | 33 | Fine | none | 6.9 | 0.2 | 18.3 | / | 3
2019-12-11 | 1655 | 1635 | / | 0 | Fine | none | 6.9 | 0.3 | 19.9 | 10.7 | 3/4
2019-12-12 | 1605 | 1449 | / | 0 | overcast/windy | none | 6.9 | 0.1 | 19.6 | 33.1 | 4
2019-12-13 |  |  | / | 0 | rain/overcast | none | 7 | 0.1 | 19.9 | / | 4/5
2019-12-14 | 1619 | 1317 | / | 0 | / | / | / | / | / | / | 5
2019-12-15 | 1620 | 1248 | / | 1 | / | / | / | / | / | / | 5
2019-12-16 | 1527 | 1270 | / | 0 | fine | none | 7 | 0.1 | 19.9 | / | 5/6
2019-12-17 | 1679 | 1319 | / | 0 | fine | none | 7.1 | 0.1 | 19.9 | 23 | 6
2019-12-18 | 1728 | 1834 | / | 1 | fine | none | 7.1 | 0.3 | 19 | / | 6/1
2019-12-19 | 1635 | 1669 | / | 12 | fine | none | 7.1 | 0.2 | 19 | / | 1
2019-12-20 | 1954 | 1674 | / | 11 | fine | none | 7 | 0.2 | 18.5 | 30.2 | 1/2
2019-12-21 | 1865 | 1845 | / | 0 | / | / | / | / | / | / | 2
2019-12-22 | 1803 | 1638 | / | 15 | / | / | / | / | / | / | 2
2019-12-23 | 1773 | 1567 | / | 0 | fine | none | 6.9 | 0.2 | 19.5 | / | 2/3
2019-12-24 | 1741 | 1480 | / | 0 | fine | none | 6.8 | 0.1 | 19.3 | / | 3
2019-12-25 | 1616 | 1416 | / | 0 | fine |  | 6.9 | 0.5 | 18.9 | / | 3/4
2019-12-26 | 1702 | 1347 | / | 0 | overcast |  | / | / | / |  | 4
2019-12-27 | 1708 | 1356 | / | 0 | overcast |  | 6.9 | 0.3 | 19.9 | / | 4/5
2019-12-28 |  |  |  | 0 | fine |  | / | / | / |  | 5
2019-12-29 | 1645 | 1346 | 23 | 0 | fine |  | / | / | / | 22.5 | 5
2019-12-30 | 1612 | 1328 |  | 1 | overcast | none | 6.9 | 0.1 | 19.8 |  | 5/6
2019-12-31 | 1671 | 1385 |  | 0 | fine | none | 6.8 | 0.1 | 19.9 |  | 6
2020-01-01 | 1528 | 1382 |  | 3 | fine | none | 7.1 | 0.1 | 20.4 |  | 6/1
2020-01-02 | 1586 | 1260 | 23 | 0 | fine | none | 7 | 0.2 | 19.6 | 57.5 | 1
2020-01-03 |  |  |  | 0 | fine | none | 7 | 0.1 | 19.7 |  | 1/2
2020-01-04 | 1653 | 1483 | / | 4 | / | / | / | / | / | / | 2
2020-01-05 | 1503 | 1341 | / | 1 | / | / | / | / | / | / | 2
2020-01-06 | 1613 | 1246 | / | 0 | fine | none | 7.1 | 0.2 | 19.1 | 50 | 2/3
2020-01-07 | 1569 | 1148 | / | 1 | fine | none | 7.1 | 0.2 | 18.9 | 24.2 | 3
2020-01-08 | 1538 | 983 | / | 0 | fine | none | 7.1 | 0.2 | 18.5 | / | 3/4
2020-01-09 | 1564 | 908 | / | 0 | fine | none | 7.3 | 0.2 | 19.8 | 21.3 | 4
2020-01-10 | 1546 | 1180 | / | 0 | fine | none | 7.2 | 0.2 | 20.1 | / | 4/5
2020-01-11 | 1547 | 1572 | 24 | 0 | Fine | none | / | / | / | 21.7 | 5
2020-01-12 | 1494 | 1343 | / | 0 | Overcast | none | / | / | / | / | 5
2020-01-13 | 1727 | 1391 | / | 0 | rain | none | 7.2 | 0.2 | 20 | / | 5/6
2020-01-14 | 1587 | 1288 | 23 | 0 | fine | none | 7.2 | 0.2 | 19.8 | 23.6 | 6
2020-01-15 | 1522 | 1670 | / | 18 | fine | / | 7.3 | 0.2 | 19.7 | / | 6/1
2020-01-16 | 1478 | 1337 | / | 1 | fine | / | 7 | 0.3 | 19.7 | / | 1
2020-01-17 | 1502 | 1202 | / | 0 | fine | / | 7 | 0.6 | 19.7 | / | 1/2
2020-01-18 | 1504 | 1141 | / | 0 | fine | / | / | / | / | / | 2
2020-01-19 | 1511 | 1158 | / | 0 | fine | / | / | / | / | / | 2
2020-01-20 | 1499 | 1190 | / | 0 | fine | / | 7.2 | 0.5 | 19.9 | / | 2/3
2020-01-21 | 1406 | 1129 | / | 0 | fine | / | 7.4 | 0.4 | 20.1 | 21.3 | 3
2020-01-22 | 1370 | 1051 | 23 | 0 | overcast | none | 7.1 | 0.2 | 21.5 | 31.5 | 3/4
2020-01-23 | 1359 | 1110 |  | 0 | overcast | none | 7.1 | 0.1 | 20.6 |  | 4
2020-01-24 |  |  |  | 0 | Fine | none | 7.1 | 0.2 | 21.4 | / | 4/5
2020-01-25 |  |  |  | 0 |  |  | / | / | / | / | 5
2020-01-26 | 1432 | 1153 | 23 | 0 |  |  | / | / | / | 10.5 | 5
2020-01-27 | 1418 | 1200 | 15 | 0 | overcast | none | 7.2 | 0.1 | 20.3 | 59.7 | 5/6
2020-01-28 | 1417 | 1236 | / | 0 | drizzle | none | 6.9 | 0.1 | 21 |  | 6
2020-01-29 | 1470 | 1310 | / | 4 | overcast | none | 6.7 | 0.2 | 20.9 |  | 6/1
2020-01-30 | 1658 | 1516 | / | 1 | overcast | none | 6.7 | 0.3 | 21 |  | 1
2020-01-31 | 1517 | 1739 | / | 3 | fine | none | 6.6 | 0.2 | 20.8 |  | 1/2
2020-02-01 | 1560 | 1437 | 24 | 8 | [5 empty] | 72.1 | 2
2020-02-02 | 1505 | 1312 | 23 | 0 | [5 empty] | 23 | 2
2020-02-03 | 1492 | 1281 |  | 0 |  |  | 6.6 | 0.4 | 20.6 |  | 2/3
2020-02-04 | 1553 | 1302 | 23 | 0 | Fine | None | 6.7 | 0.5 | 21.3 | 8.2 | 3
2020-02-05 | 1501 | 1287 | 23 | 0 | Fine | None | 6.7 | 0.2 | 20.2 |  | 3/4
2020-02-06 | 1606 | 1233 |  | 3 | Fine | None | 6.6 | 0.1 | 20.4 |  | 4
2020-02-07 | 1534 | 1161 |  | 0 | Fine | None | 6.8 | 0.1 | 20.9 |  | 4/5
2020-02-08 | 1582 | 814 |  | 0 | overcast | None | / | / | / |  | 5
2020-02-09 | 1668 | 732 | 23 | 0 | Fine | None | / | / | / |  | 5
2020-02-10 | 1538 | 743 | 17 | 2 | Fine | None | 6.8 | 0.1 | 21 | 71.3 | 5/6
2020-02-11 | 1425 | 2231 | 25 | 0 | overcast | None | 6.8 | 0.1 | 20.5 | 27 | 6
2020-02-12 | 1468 | 1627 | 24 | 0 | Fine | None | 6.7 | 0.1 | 21.3 | 35.8 | 6/1
2020-02-13 | 1437 | 1361 | 24 | 0 | Overcast | None | 6.7 | 0.1 | 20.8 | 37.8 | 1
2020-02-14 | 1456 | 1233 | 23 | 0 | Fine | None | 6.7 | 0.1 | 21.4 | 29.6 | 1/2
2020-02-15 | 1493 | 1199 | 24 | 0 | Fine | None | / | / | / | 24.4 | 2
2020-02-16 | 1449 | 1192 | 23 | 0 | Fine | None | / | / | / | 0 | 2
2020-02-17 | 1387 | 1214 | 18 | 0 | Overcast/Wet | None | 6.8 | 0.1 | 21.9 |  | 2/3
2020-02-18 | 1478 | 1271 | 24 | 0 | wet | none | 6.7 | 0.1 | 20.3 | 28.3 | 3
2020-02-19 | 1532 | 1512 | 24 | 3 | overcast/wet | none | 6.7 | 0.4 | 20.9 | 33.3 | 3/4
2020-02-20 | 1533 | 1408 | 24 | 6 | fine | none | 6.7 | 0.3 | 21.2 | 40.9 | 4
2020-02-21 | 1484 | 1351 |  | 5 | Fine | none | 6.8 | 0.2 | 21.1 |  | 4/5
2020-02-22 | 1475 | 1227 |  | 0 | fine | none | / | / | / | / | 5
2020-02-23 | 1687 | 1346 | 22 | 0 | fine | none | / | / | / | 46.8 | 5
2020-02-24 | 1575 | 1345 | 23 | 0 | fine | none | 7.1 | 0.2 | 20.1 | 23.6 | 5/6
2020-02-25 | 1489 | 1241 |  | 9 | fine | none | 6.8 | 0.3 | 20.2 |  | 6
2020-02-26 | 1436 | 786 |  | 0 | fine | none | 7 | 0.3 | 20.8 |  | S/B
2020-02-27 | 1436 | 0 |  | 0 | fine | none | 7 | 2.5 | 21.6 |  | S/B
2020-02-28 | 1458 | 1623 | 23 | 0 | fine | none | 7 | 2.6 | 21.4 | 24.9 | 1
2020-02-29 | 1651 | 2014 | 23 | 0 | Fine | none | / | / | / | 26.1 | 1
2020-03-01 | 1613 | 1913 |  | 0 | fine | none | / | / | / | / | 1
2020-03-02 | 1463 | 1431 |  | 12 | fine | none | 6.9 | 2.5 | 22.1 |  | 1/2
2020-03-03 | 1433 | 1273 |  | 0 | overcast / Light breeze | none | 7.2 | 2.6 | 20.8 |  | 2
2020-03-04 | 1581 | 1503 |  | 0 | fine | none | 7.2 | 0.2 | 20.6 |  | 2/3
2020-03-05 | 1566 | 1033 | 24 | 0 | fine/windy | none | 7.2 | 0.2 | 20.6 |  | 3
2020-03-06 | 1496 | 804 |  | 6 |  | none | 7.1 | 0.2 | 19.7 |  | 3/5
2020-03-07 | 1543 | 1431 | 25 | 0 |  | none | / | / | / |  | 5
2020-03-08 | 1517 | 1206 |  | 0 |  | none | / | / | / |  | 5
2020-03-09 | 1549 | 1187 | 22 | 0 | overcast/light rain | none | 7.1 | 0.2 | 19.9 |  | 5
2020-03-10 | 1526 | 1352 | 13 | 0 |  | none | 7 | 0.2 | 19.6 |  | 5
2020-03-11 | 1527 | 1238 | 29 | 10 |  | none | 7 | 0.4 | 19.8 |  | 5
2020-03-12 | 1538 | 1163 | 24 | 0 |  | none | 7.1 | 0.3 | 19.2 |  | 5
2020-03-13 | 1527 | 1263 | 23 | 0 | fine | none | 7.3 | 0.2 | 19.2 |  | 5
2020-03-14 | 1564 | 1265 | 23 | 0 |  | none | / | / | / |  | 6
2020-03-15 | 1551 | 1281 | 21 | 0 |  | none | / | / | / |  | 6
2020-03-16 | 1475 | 1320 | 52 | 0 | fine | none | 6.9 | 0.2 | 19.9 |  | 6
2020-03-17 | 1442 | 737 | 25 | 0 | fine | none | 6.8 | 0.2 | 19.8 |  | 6
2020-03-18 | 1461 | 751 | 24 | 0 | fine | none | 7 | 1.9 | 18.6 |  | 6
2020-03-19 | 1429 | 1925 |  | 0 | fine | none | 6.9 | 0.2 | 19.4 |  | 6
2020-03-20 | 1430 | 2268 |  | 0 | overcast | none | 7 | 0.3 | 19.1 |  | 6
2020-03-21 | 1496 | 1705 |  | 1 | overcast | none | / | / | / |  | 6
2020-03-22 | 1598 | 1447 | 24 | 0 |  | none | / | / | / |  | 6
2020-03-23 | 1757 | 1270 | 23 | 0 | fine/overcast | none | 7 | 0.3 | 20.1 | 38.9 | 6
2020-03-24 | 1604 | 1566 |  | 5 | fine | none | 7.4 | 0.2 | 19.1 |  | 6
2020-03-25 | 1612 | 1408 |  | 16 | fine/overcast | none | 7.2 | 0.2 | 18.8 |  | 6
2020-03-26 | 1583 | 1332 |  | 0 | overcast | none | 6.9 | 0.4 | 18.9 |  | 6
2020-03-27 | 1559 | 1234 |  | 0 | rain | none | 7 | 0.3 | 18.5 |  | 6
2020-03-28 | 2072 | 2232 |  | 5 | rain | none | / | / | / |  | 6
2020-03-29 | 1790 | 1211 |  | 4 |  | none | / | / | / |  | 6
2020-03-30 | 1858 | 1286 | 23 | 24 | fine | none | 6.9 | 0.4 | 17.9 |  | 6
2020-03-31 | 1712 | 1497 | 23 | 1 | fine | none | 7 | 0.3 | 17.8 |  | 6
2020-04-01 | 1686 | 2685 | 23 | 0 | fine | none | 6.4 | 3.1 | 18.1 |  | 6
2020-04-02 | 1630 | 2578 | 23 | 1 | overcast | none | 6.8 | 0.5 | 18.6 |  | 6
2020-04-03 | 1607 | 2026 | 23 | 0 | fine | none | 7 | 0.3 | 18.2 |  | 6
2020-04-04 | 1607 | 1652 | / | 0 | fine | none | / | / | / | / | 1
2020-04-05 | 1604 | 1517 | 24 | 0 | fine | none | / | / | / | / | 1
2020-04-06 | 1562 | 1307 | 20 | 0 | fine | none | 7 | 0.4 | 18.3 | 48 | 1/5
2020-04-07 | 1498 | 1272 |  | 0 | fine | none | 7.5 | 0.3 | 18.5 |  | 1/5
2020-04-08 | 1517 | 1353 |  | 0 | fine | none | 7.3 | 0.4 | 18.4 |  | 3
2020-04-09 | 1537 | 1279 | 24 | 2 | fine morning rain | none | 7.1 | 0.3 | 18.4 | 26 | 3
2020-04-10 | 1575 | 1219 | 23 | 8 | fine | none | 7.1 | 0.3 | 18.2 |  | 3
2020-04-11 | 1569 | 1333 |  | 0 | fine | none | / | / | / | / | 3
2020-04-12 | 1449 | 1545 |  | 0 | fine overnight rain | none | / | / | / | / | 3
2020-04-13 | 1730 | 1655 | 22 | 0 | fine windy | none | 7.2 | 0.1 | 18.4 |  | 3
2020-04-14 | 1513 | 1416 |  | 5 | fine/windy | none | 7.1 | 0.1 | 16.8 | / | 3
2020-04-15 | 1570 | 1433 |  | 9 |  | none | 7.2 | 0.2 | 16.5 | / | 3
2020-04-16 | 1513 | 1416 |  | 0 |  | none | 7.1 | 0.1 | 17.1 | / | 3
2020-04-17 | 1549 | 1340 |  | 0 |  | none | 7.1 | 0.1 | 16.8 | / | 6
2020-04-18 | 1568 | 1572 |  | 0 |  | none | / | / | / |  | 6
2020-04-19 | 1690 | 1573 |  | 8 |  | none | / | / | / |  | 6
2020-04-20 | 1653 | 1557 |  | 1 |  | none | 6.9 | 0.2 | 17.4 | / | 6
2020-04-21 | 1629 | 1558 | 24 | 3 | fine/windy | none | 6.9 | 0.2 | 17.6 | 17.3 | 6
2020-04-22 | 1580 | 1524 | 23 | 1 | fine/sunny | none | 6.9 | 0.2 | 17.5 | 21 | 6
2020-04-23 | 1528 | 1496 | 24 | 1 | fine | none | 7 | 0.1 | 17.7 | 26.5 | 6
2020-04-24 | 1544 | 1430 | 23 | 0 | fine/overcast | none | 7.1 | 0.3 | 17.9 | 23.7 | 6
2020-04-25 | 1518 | 1391 | 23 | 0 | fine/overcast | none | / | / | / | 19.6 | 6
2020-04-26 | 1559 | 1346 | 24 | 1 | fine/overcast | none | / | / | / | 25.2 | 6
2020-04-27 | 1473 | 1358 | 23 | 0 | overcast | none | 7 | 0.3 | 17.9 | 43 | 6
2020-04-28 | 1567 | 1314 | 22 | 0 | fine/sunny | none | 7.1 | 0.3 | 17.6 | 29.3 | 6
2020-04-29 | 1565 | 1381 | 23 | 0 |  | none | 7.1 | 0.2 | 17.8 | 29.3 | 6
2020-04-30 | 1467 | 1358 | 24 | 0 |  | none | 7 | 0.1 | 17.6 | 19.3 | 6
2020-05-01 | 1477 | 1325 | 23 | 0 |  | none | 7.1 | 0.1 | 17.3 | 23.3 | 6
2020-05-02 | 1523 | 1299 | 16 | 0 |  | none | / | / | / | 20.6 | 6
2020-05-03 | 2677 | 1296 | 14 | 0 |  | none | / | / | / | 0 | 6
2020-05-04 | 2218 | 2800 | 27 | 0 | overcast/rain | none | 7 | 0.3 | 17.4 | 10.9 | 6
2020-05-05 | 2265 | 2800 | 3 | 42 | rain/overcast | none | 6.9 | 0.2 | 17 | 0 | 6
2020-05-06 | 2218 | 2751 |  | 17 | sunny | none | 7 | 0.3 | 17.5 | 33.5 | 6
2020-05-07 | 1930 | 2307 |  | 8 | fine | none | 6.9 | 0.2 | 17.2 | 35.2 | 6
2020-05-08 | 1875 | 1991 | 25 | 0 | fine | none | 7 | 0.2 | 17.4 | 27 | 5
2020-05-09 |  | 1833 | 23 | 0 | overcast | none | / | / | / | 15.1 | 5
2020-05-10 |  | 1766 | 24 | 0 | sunny | none | / | / | / |  | 5
2020-05-11 | 778 | 1552 | 23 | 0 | fine/overcast | none | 7.1 | 0.3 | 17.2 | 28.9 | 5
2020-05-12 | 1658 | 1665 | 24 | 0 | fine | none | 6.9 | 0.3 | 16.8 | 7.1 | 5
2020-05-13 | 1661 | 1893 | 23 | 0 | fine | none | 7 | 0.2 | 16.6 | 26.5 | 5
2020-05-14 | 1633 | 1443 | 23 | 0 | fine | none | 7 | 0.3 | 16.3 | 35.1 | 4
2020-05-15 | 1624 | 1856 |  | 0 | Fine | none | 6.9 | 0.3 | 16.5 |  | 4
2020-05-16 | 1677 | 1659 |  | 0 | Fine | none | / | / | / |  | 4
2020-05-17 | 1707 | 1574 | 23 | 0 | fine | none | / | / | / | 3 | 4
2020-05-18 | 1636 | 1419 | 16 | 0 | Fine | none | 7.6 | 0.4 | 16.3 | 39.4 | 4/3
2020-05-19 | 1579 | 1623 | 25 | 0 | Fine | none | 6.9 | 0.3 | 16.4 | 20.8 | 3
2020-05-20 | 1590 | 1486 | 24 | 0 | Fine | none | 7 | 0.1 | 15.8 | 23.8 | 3
2020-05-21 | 1522 | 1447 | 24 | 0 | Fine | none | 6.9 | 0.2 | 15.1 | 13.2 | 3
2020-05-22 | 1540 | 1457 |  | 0 | Fine | none | 7 | 0.2 | 15.7 |  | 3/2
2020-05-23 | 1657 | 1471 | / | 0 | overcast | none | / | / | / | / | 2
2020-05-24 | 1645 | 1500 | 24 | 0 | Raining | None | / | / | / | 10.9 | 2
2020-05-25 | 2171 | 1796 | 23 | 0 | wet | none | 7.1 | 0.2 | 14.8 | 28.2 | 2/1
2020-05-26 | 1807 | 2000 |  | 12 | Fine | none | 6.9 | 0.1 | 16.3 |  | 1
2020-05-27 | 1692 | 2386 |  | 22 |  |  | 6.9 | 0.3 | 15.7 |  | 1/5
2020-05-28 | 1586 | 1913 | 23 | 0 |  |  | 6.8 | 0.2 | 15.2 | 24.7 | 5
2020-05-29 | 1641 | 1671 |  | 0 |  |  | 7 | 0.3 | 15 |  | 5
2020-05-30 | 1594 | 1690 | 23 | 0 | fine | none | / | / | / | 38.5 | 5
2020-05-31 | 1666 | 1591 | 24 | 3 | fine | none | / | / | / | 0 | 5
2020-06-01 | 1652 | 1574 |  | 1 | Wet | none | 7.1 | 0.2 | 14.8 |  | 5/4
2020-06-02 | 1579 | 1789 |  | 0 | overcast/rain | none | 7.1 | 0.3 | 16.1 |  | 4
2020-06-03 | 1576 | 1627 |  | 5 | rain/sunny | none | 7.1 | 0.3 | 16.2 |  | 4
2020-06-04 | 2326 | 1808 |  | 0 | fine | none | 7.2 | 0.2 | 16 |  | 4
2020-06-05 | 2917 | 2801 |  | 3 | overcast | none | 7.2 | 0.2 | 14.9 | 3.5 | 4
2020-06-06 | 2128 | 2803 | 23 | 32 | fine | none | / | / | / |  | 4
2020-06-07 | 1992 | 2801 | 12 | 15 | fine | none | / | / | / |  | 4
2020-06-08 | 1842 | 2313 | 17 | 1 | fine | none | 7.1 | 0.3 | 15.3 |  | 4/3
2020-06-09 | 1744 | 1946 | 20 | 0 | fine | none | 6.9 | 0.3 | 15.2 | 17.3 | 3
2020-06-10 | 1639 | 1589 | 24 | 0 | fine/sunny | none | 6.9 | 0.4 | 14.9 | 20.5 | 3
2020-06-11 | 1605 | 1820 | 31 | 0 | overcast | none | 7.1 | 0.4 | 14.8 | 6.9 | 3
2020-06-12 | 1580 | 1665 | 22 | 0 | overcast | none | 7 | 0.3 | 15.1 | 39.3 | 3/2
2020-06-13 | 1720 | 1558 |  | 0 | fine | none | / | / | / |  | 2
2020-06-14 | 1692 | 1513 | 24 | 0 | fine | none | / | / | / | 0 | 2
2020-06-15 | 1531 | 1542 | 23 | 0 | overcast/drizzle | none | 7.6 | 0.3 | 14.5 | 26.3 | 2/1
2020-06-16 | 1555 | 1641 | 24 | 0 | overcast/drizzle | none | 7 | 0.4 | 15.1 | 24 | 1
2020-06-17 | 1668 | 1659 | 23 | 1 | Overcast/Drizzle | none | 7.1 | 0.2 | 14.8 | 24 | 1/5
2020-06-18 | 3326 | 2195 | 23 | 3 | Raining | none | 7 | 0.1 | 15.1 | 26 | 5
2020-06-19 | 2957 | 2647 | 24 | 3 | overcast/drizzle | none | 7 | 0.1 | 15 | 20.7 | 5/4
2020-06-20 | 2518 | 2312 | 23 | 46 | Fine | none | / | / | / | 18.4 | 4
2020-06-21 | 2296 | 1967 | 24 | 9 | Fine | none | / | / | / | 22.2 | 4
2020-06-22 | 2059 | 2347 | 23 | 1 | Fine | none | 6.8 | 0.2 | 14.7 | 28.2 | 4/3
2020-06-23 | 1886 | 2808 | 23 | 0 | Fine | none | 6.8 | 0.1 | 14.8 | 27.4 | 3/4
2020-06-24 | 1835 | 2801 | 24 | 0 | fine | none | 6.9 | 0.3 | 15 | 19.2 | 3/5
2020-06-25 | 1708 | 2227 | 23 | 0 | overcast | none | 6.8 | 0.2 | 14.8 | 22.9 | 2/1
2020-06-26 | 1708 | 1825 |  | 0 | overcast | none | 6.9 | 0.2 | 14.9 |  | 1
2020-06-27 | 1666 | 1681 |  | 0 | overcast | none | / | / | / |  | 1
2020-06-28 | 1922 | 1796 | 23 | 0 | fine | none | / | / | / | 16.3 | 1
2020-06-29 | 1860 | 2114 | 23 | 0 | overcast/showers | none | 7 | 3.5 | 14 | 42.5 | 1/5
2020-06-30 | 1809 | 2148 |  | 15 |  | none | 6.9 | 3.2 | 13.9 |  | 5

## Ponds A & B Effluent
Pond A Effluent | [15 empty] | >8 out of 12 | >2 out of 12
SampleDate | SiteID | LogNo | BOD | SBOD5 | SCBOD5 | TSS | pH | AmmN | NitraN | DRP | TotalP | TN | Faecal | EColi | Limits | ScBOD | ScBOD | TSS | TSS | Faecal | Faecal | NH4-N | NH4-N | DRP | DRP
2019-07-12 | Pond A | 193010 | 52.9 | 6.9 | 3.7 | 80 | 7.8 | 30 | <0.2 | 3.5 | 5.2 | 45 | 90000 | 80000 | 2019-06-15 | 35 | 45 | 100 | 150 | 50000 | 120000 | 23 | 30 | 5 | 11
2019-08-13 | Pond A | 193469 | 27.1 | 5.8 | 4.1 | 34.8 | 7.7 | 22 | 0.2 | 2.9 | 3.7 | 32 | 129000 | 100000 | 2020-06-30 | 35 | 45 | 100 | 150 | 50000 | 120000 | 23 | 30 | 5 | 11
2019-09-24 | Pond A | 194081 | 13.2 | 8.2 | 3.9 | 4.6 | 7.4 | 36.5 | 0.2 | 4.6 | - | - | 4800 | 3300
2019-10-24 | Pond A | 194520 | 10.7 | 5.9 | 2.4 | 7.3 | 7.6 | 33.4 | 0.2 | 4.2 | 4.7 | 37 | 2050 | 1900 | Note: New trainee lab assistant, no TotalP or TN tested. Employee was spoken to, and this mistake was not made again.
2019-11-27 | Pond A | 195088 | 45.1 | 5.6 | 2.4 | 60.8 | 8.8 | 19.3 | 0.3 | 3.7 | 4.6 | 48 | 5000 | 4500
2019-12-10 | Pond A | 195303 | 11.6 | 6.6 | 4.3 | 18.8 | 7.6 | 27.2 | 0.3 | 4.5 | 4.4 | 30 | 3000 | 2000
2020-01-23 | Pond A | 200311 | 31.7 | 7 | 2.1 | 37.6 | 7.6 | 24 | 0.2 | 4.5 | 4.9 | 27 | 17000 | 15000
2020-02-17 | Pond A | 200745 | 16.4 | 4.9 | 2 | 33.8 | 8 | 24.1 | 0.3 | 17.7 | 5.4 | 33 | 20000 | 17000
2020-03-04 | Pond A | 201064 | 11.5 | 4.9 | 1.8 | 21.4 | 7.6 | 24.4 | <0.2 | 5.1 | 5.2 | 28 | 8500 | 5800
2020-04-23 | Pond A | 201717 | 34 | 4.9 | 2.3 | 48.6 | 7.5 | 27.2 | <0.2 | 5 | 4.9 | 39 | 56000 | 39000
2020-05-12 | Pond A | 201943 | 20.6 | 5.4 | 4.2 | 32.8 | 7.4 | 29.2 | <0.2 | 5.3 | 5.7 | 38 | 17000 | 9000
2020-06-05 | Pond A | 202294 | 22.3 | 6.8 | 5.9 | 37.2 | 8.4 | 29.7 | <0.2 | 3.8 | 4.9 | 34 | 58000 | 29000
Pond B Effluent
SampleDate | SiteID | LogNo | BOD | SBOD5 | SCBOD5 | TSS | pH | AmmN | NitraN | DRP | TotalP | TN | Faecal | EColi
2019-07-12 | Pond B | 193011 | 29.3 | 5.4 | 3.5 | 44.4 | 7.9 | 31.4 | <0.2 | 4.9 | 5.3 | 40 | 180000 | 160000
2019-08-13 | Pond B | 193470 | 24.9 | 6.5 | 5 | 41.8 | 8.1 | 19.9 | 0.3 | 2.7 | 3.5 | 23 | 170000 | 120000
2019-09-24 | Pond B | 194082 | 13.7 | 9.4 | 3.4 | 8.9 | 7.3 | 30.7 | 0.2 | 4.2 | - | - | 23000 | 20000
2019-10-24 | Pond B | 194521 | 6.7 | 4.7 | 1.7 | 0.3 | 7.7 | 33.7 | 0.3 | 4.4 | 4.7 | 41 | 550 | 450
2019-11-27 | Pond B | 195089 | 19.5 | 5.2 | 1.1 | 40.8 | 8.4 | 26.8 | 0.3 | 5 | 5.1 | 59 | 52000 | 30000
2019-12-10 | Pond B | 195304 | 17.2 | 3.5 | 1.7 | 35 | 7.8 | 23.9 | 0.3 | 4.2 | 4.2 | 28 | 22000 | 12000
2020-01-23 | Pond B | 200312 | 14.4 | 8.1 | 3.7 | 32 | 8.5 | 22.1 | 0.3 | 4.9 | 5.3 | 26 | 9100 | 6800
2020-02-17 | Pond B | 200746 | 38.9 | 8.2 | 2.8 | 45.8 | 7.3 | 23.3 | 0.3 | 12.4 | 6.2 | 31 | 900 | 900
2020-03-04 | Pond B | 201065 | 19.3 | 10.6 | 6.6 | 15.8 | 7.8 | 26.6 | 0.3 | 10.2 | 5.3 | 34 | 53000 | 42000
2020-04-23 | Pond B | 201718 | 25.4 | 5.6 | 2.4 | 39.6 | 7.6 | 29.9 | <0.2 | 4.2 | 5.2 | 34 | 44000 | 34000
2020-05-12 | Pond B | 201944 | 16.2 | 5.2 | 4.5 | 21 | 7.6 | 32 | <0.2 | 4.6 | 4.8 | 35 | 8000 | 7000
2020-06-05 | Pond B | 202295 | 28.1 | 4.8 | 3.1 | 33.2 | 7.4 | 32.1 | <0.2 | 14 | 4.5 | 32 | 22000 | 16000
Weekly DO
| Pond A | Pond B
SampleDate | DO | DO
2019-07-04 | 6.2 | 6.1
2019-07-12 | 5.5 | 9.6
2019-07-17 | 7.1 | 8.1
2019-07-27 | 0.6 | 9
2019-08-08 | 6.3 | 11.9
2019-08-09 | 13.2 | 16.6
2019-08-13 | 4.3 | 6.3
2019-08-19 | 10.9 | 15.6
2019-08-30 | 7.5 | 10.4
2019-09-03 | 4.9 | 8.5
2019-09-09 | 3.1 | 13.4
2019-09-19 | 1.4 | 1.6
2019-09-24 | 1.9 | 0.6
2019-10-01 | 2.9 | 0.1
2019-10-07 | 1.6 | 2
2019-10-16 | 1.7 | 1.6
2019-10-24 | 3.9 | 3.5
2019-11-01 | 16.2 | 8.9
2019-11-05 | 12.5 | 9
2019-11-15 | 6 | 3.3
2019-11-27 | 13.6 | 12
2019-12-06 | 5.5 | 8.5
2019-12-10 | 10.5 | 8.9
2019-12-18 | 13.5 | 8.6
2019-12-27 | 9.8 | 16.8
2020-01-07 | 7.2 | 12.2
2020-01-17 | 16.2 | 25.8
2020-01-23 | 0.8 | 6.7
2020-01-30 | 4.4 | 2.1
2020-02-04 | 2 | 3.4
2020-02-12 | 24.1 | 11.9
2020-02-17 | 4.1 | 0.9
2020-02-27 | 8.7 | 4.7
2020-03-04 | 1.9 | 3
2020-03-09 | 2.8 | 1.8
2020-03-19 | 1.3 | 1.2
2020-03-23 | 2.6 | 1.3
2020-04-06 | 2.6 | 9.7
2020-04-15 | 10.5 | 11.8
2020-04-23 | 1.8 | 4.6
2020-04-28 | 1.5 | 3.1
2020-05-05 | 1.3 | 2.8
2020-05-12 | 2.4 | 5.6
2020-05-19 | 8.2 | 12.2
2020-05-29 | 7.1 | 7.3
2020-06-05 | 4.8 | 3.6
2020-06-10 | 6.6 | 11.6
2020-06-18 | 3.7 | 5.4
2020-06-22 | 8.5 | 11.8
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.

## Pond A
Pond A Effluent | [15 empty] | >8 out of 12 | >2 out of 12
SampleDate | SiteID | LogNo | BOD | SBOD5 | SCBOD5 | TSS | pH | AmmN | NitraN | DRP | TotalP | TN | Faecal | EColi | Limits | ScBOD | ScBOD | TSS | TSS | Faecal | Faecal | NH4-N | NH4-N | DRP | DRP
2019-07-12 | Pond A | 193010 | 52.9 | 6.9 | 3.7 | 80 | 7.8 | 30 | <0.2 | 3.5 | 5.2 | 45 | 90000 | 80000 | 2019-06-15 | 35 | 45 | 100 | 150 | 50000 | 120000 | 23 | 30 | 5 | 11
2019-08-13 | Pond A | 193469 | 27.1 | 5.8 | 4.1 | 34.8 | 7.7 | 22 | 0.2 | 2.9 | 3.7 | 32 | 129000 | 100000 | 2020-07-01 | 35 | 45 | 100 | 150 | 50000 | 120000 | 23 | 30 | 5 | 11
2019-09-24 | Pond A | 194081 | 13.2 | 8.2 | 3.9 | 4.6 | 7.4 | 36.5 | 0.2 | 4.6 | - | - | 4800 | 3300 | 2020-11-30 | 35 | 45 | 100 | 150 | 50000 | 120000 | 23 | 30 | 5 | 11
2019-10-24 | Pond A | 194520 | 10.7 | 5.9 | 2.4 | 7.3 | 7.6 | 33.4 | 0.2 | 4.2 | 4.7 | 37 | 2050 | 1900
2019-11-27 | Pond A | 195088 | 45.1 | 5.6 | 2.4 | 60.8 | 8.8 | 19.3 | 0.3 | 3.7 | 4.6 | 48 | 5000 | 4500 | Note: New trainee lab assistant, no TP or TN tested. Employee was spoken to, and this mistake was not made again.
2019-12-10 | Pond A | 195303 | 11.6 | 6.6 | 4.3 | 18.8 | 7.6 | 27.2 | 0.3 | 4.5 | 4.4 | 30 | 3000 | 2000
2020-01-23 | Pond A | 200311 | 31.7 | 7 | 2.1 | 37.6 | 7.6 | 24 | 0.2 | 4.5 | 4.9 | 27 | 17000 | 15000
2020-02-17 | Pond A | 200745 | 16.4 | 4.9 | 2 | 33.8 | 8 | 24.1 | 0.3 | 17.7 | 5.4 | 33 | 20000 | 17000
2020-03-04 | Pond A | 201064 | 11.5 | 4.9 | 1.8 | 21.4 | 7.6 | 24.4 | <0.2 | 5.1 | 5.2 | 28 | 8500 | 5800
2020-04-23 | Pond A | 201717 | 34 | 4.9 | 2.3 | 48.6 | 7.5 | 27.2 | <0.2 | 5 | 4.9 | 39 | 56000 | 39000
2020-05-12 | Pond A | 201943 | 20.6 | 5.4 | 4.2 | 32.8 | 7.4 | 29.2 | <0.2 | 5.3 | 5.7 | 38 | 17000 | 9000
2020-06-05 | Pond A | 202294 | 22.3 | 6.8 | 5.9 | 37.2 | 8.4 | 29.7 | <0.2 | 3.8 | 4.9 | 34 | 58000 | 29000
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.

## Pond B
Pond B Effluent | [15 empty] | >8 out of 12 | >2 out of 12
SampleDate | SiteID | LogNo | BOD | SBOD5 | SCBOD5 | TSS | pH | AmmN | NitraN | DRP | TotalP | TN | Faecal | EColi | Limits | ScBOD5 | ScBOD5 | TSS | TSS | Faecal | Faecal | NH4-N | NH4-N | DRP | DRP
2019-07-12 | Pond B | 193011 | 29.3 | 5.4 | 3.5 | 44.4 | 7.9 | 31.4 | <0.2 | 4.9 | 5.3 | 40 | 180000 | 160000 | 2019-06-15 | 35 | 45 | 100 | 150 | 50000 | 120000 | 23 | 30 | 5 | 11
2019-08-13 | Pond B | 193470 | 24.9 | 6.5 | 5 | 41.8 | 8.1 | 19.9 | 0.3 | 2.7 | 3.5 | 23 | 170000 | 120000 | 2020-07-01 | 35 | 45 | 100 | 150 | 50000 | 120000 | 23 | 30 | 5 | 11
2019-09-24 | Pond B | 194082 | 13.7 | 9.4 | 3.4 | 8.9 | 7.3 | 30.7 | 0.2 | 4.2 | - | - | 23000 | 20000 | 2020-11-30 | 35 | 45 | 100 | 150 | 50000 | 120000 | 23 | 30 | 5 | 11
2019-10-24 | Pond B | 194521 | 6.7 | 4.7 | 1.7 | 0.3 | 7.7 | 33.7 | 0.3 | 4.4 | 4.7 | 41 | 550 | 450
2019-11-27 | Pond B | 195089 | 19.5 | 5.2 | 1.1 | 40.8 | 8.4 | 26.8 | 0.3 | 5 | 5.1 | 59 | 52000 | 30000
2019-12-10 | Pond B | 195304 | 17.2 | 3.5 | 1.7 | 35 | 7.8 | 23.9 | 0.3 | 4.2 | 4.2 | 28 | 22000 | 12000 | Note: New trainee lab assistant, no TP or TN tested. Employee was spoken to, and this mistake was not made again.
2020-01-23 | Pond B | 200312 | 14.4 | 8.1 | 3.7 | 32 | 8.5 | 22.1 | 0.3 | 4.9 | 5.3 | 26 | 9100 | 6800
2020-02-17 | Pond B | 200746 | 38.9 | 8.2 | 2.8 | 45.8 | 7.3 | 23.3 | 0.3 | 12.4 | 6.2 | 31 | 900 | 900
2020-03-04 | Pond B | 201065 | 19.3 | 10.6 | 6.6 | 15.8 | 7.8 | 26.6 | 0.3 | 10.2 | 5.3 | 34 | 53000 | 42000
2020-04-23 | Pond B | 201718 | 25.4 | 5.6 | 2.4 | 39.6 | 7.6 | 29.9 | <0.2 | 4.2 | 5.2 | 34 | 44000 | 34000
2020-05-12 | Pond B | 201944 | 16.2 | 5.2 | 4.5 | 21 | 7.6 | 32 | <0.2 | 4.6 | 4.8 | 35 | 8000 | 7000
2020-06-05 | Pond B | 202295 | 28.1 | 4.8 | 3.1 | 33.2 | 7.4 | 32.1 | <0.2 | 14 | 4.5 | 32 | 22000 | 16000
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.

## Bores & Spring
Bores and Spring Monitoring Data | [18 empty] | Bore 4 |  | Bore 5 |  |  | Bore 4 |  |  | Bore 5 |  |  | Spring
Sample Date | SiteID | LogNo | Depth | Temp | pH | Conduct | BOD | Amm-N | Nitrate | Nitrite | DRP | Chloride | TP | TN | TN 0.45 | F/coli | Ecoli | Sample Date | Ecoli cfu/100ml | TN 0.45 (g/m³) | Ecoli cfu/100ml | TN 0.45 Filter (g/m³) | Sample Date | TN (g/m³) | DRP (g/m³) | Ecoli cfu/100ml | TN (g/m³) | DRP (g/m³) | Ecoli cfu/100ml | TN (g/m³) | DRP (g/m³) | Ecoli cfu/100ml
2019-07-08 | 1 | 192930 | 4.2 | 15 | 3 | 0.07 | 0.5 | 0.11 | <0.2 |  | 0.02 | 7 | 0.02 | <1 | - | <1 | - | 2019-07-08 | - | 2 | - | 3 | 2019-07-08 | <1 | 0.2 | - | 6 | 0.25 | - | 1 | 0.03 | -
2019-08-21 | 1 | 193600 | 3.7 | 13.1 | 6.9 | 0.09 | 1.5 | <0.02 | 0.5 |  | 0.03 | 12 | 0.03 | 4 | - | 3 | 2 | 2019-08-21 | - (<1) | 2 | 5 | 9 | 2019-08-21 | 3 | 0.19 | - (<1) | 10 | 0.23 | 5 | <1 | 0.01 | -(<1)
2019-09-10 | 1 | 193882 | 3.9 | 12.6 | 6.1 | 0.08 | 0.5 | <0.02 | 0.3 |  | 0.02 | 8 | 0.03 | <1 | - | 2 | 1 | 2019-09-10 | * | 1 | 4 | 8 | 2019-09-10 | 2 | 0.18 | * | 9 | 0.3 | 4 | <1 | 0.01 | 380
2019-10-11 | 1 | 194339 | 3.57 | 11.6 | 6.1 | 0.08 | 0.3 | <0.02 | <0.2 |  | 0.01 | 8 | 0.02 | <1 | - | <1 | - | 2019-10-11 | - | <1 | 2 | 6 | 2019-10-11 | <1 | 0.22 | - | 4 | 0.04 | 2 | 1 | 0.01 | 11
2019-11-21 | 1 | 194973 | 3.85 | 11.3 | 6.4 | 0.08 | 1 | <0.02 | 0.3 |  | 0.09 | 8 | 0.02 | <1 | - | <1 | - | 2019-11-21 | - | 2 | 1 | 2 | 2019-11-21 | 6 | 0.18 | - | 5 | 0.25 | 1 | <1 | 0.02 | 110
2019-12-04 | 1 | 195205 | 3.66 | 11.3 | 6.3 | 0.08 | 0.8 | <0.02 | 0.2 |  | 0.02 | 9 | 0.05 | <1 | - | 1 | 1 | 2019-12-04 | * | <1 | 1 | 1 | 2019-12-04 | 1 | 0.17 | * | 4 | 0.25 | 1 | <1 | 0.01 | 2900
2020-01-24 | 1 | 200341 | 3.8 | 12.3 | 5.8 | 0.08 | 0.7 | 0.02 | 0.2 | <0.015 | 0.03 | 8 | 0.62 | 1 | - | 7 | 3 | 2020-01-24 | <1 | 3 | 3 | 5 | 2020-01-24 | 2 | 0.17 | <1 | 5 | 0.31 | 3 | 2 | 0.03 | 490
2020-02-18 | 1 | 200760 | 3.85 | 13.2 | 5.8 | 0.08 | 0.2 | 0.02 | 0.4 | <0.015 | 0.03 | 7 | 0.02 | <1 | - | 1 | 1 | 2020-02-18 | <1 | 3 | 159 | 2 | 2020-02-18 | 6 | 0.17 | <1 | 6 | 0.3 | 159 | <1 | <0.01 | 840
2020-03-12 | 1 | 201193 | 4.7 | 14.3 | 6.5 | 0.08 | 0.5 | <0.02 | <0.2 | <0.015 | 0.02 | 7 | 0.05 | 1 | - | <1 | <1 | 2020-03-12 | 3 | 3 | 6 | 7 | 2020-03-12 | 1 | 0.18 | 3 | 7 | 0.31 | 6 | 2 | 0.01 | 510
2020-04-07 | 1 | 201531 | 4.1 | 15.3 | 6.3 | 0.08 | 0.6 | <0.02 | 0.3 | <0.015 | 0.04 | 8 | 0.02 | 1 | - | 60 | 49 | 2020-04-07 | <1 | - | 1 | - | 2020-04-07 | <1 | 0.2 | <1 | 3 | 0.3 | 1 | 2 | 0.01 | 5600
2020-04-08 | 1 | 201554 | - | - | - | - | - | - | - | - | - | - | - | - | - | 4 | 2 | 2020-04-08 |  |  |  |  | 2020-04-08 | [6 empty] | - | - | 1000
2020-05-21 | 1 | 202072 | 3.97 | 15.3 | 6.4 | 0.08 | 2.4 | 0.03 | <0.2 | <0.015 | 0.02 | 8 | 0.03 | <1 | - | 1 | 1 | 2020-05-21 | - | <1 | - | <1 | 2020-05-21 | <1 | 0.36 | - | <1 | 0.35 | - | <1 | 0.02 | 2
2020-06-15 | 1 | 202424 | 3.9 | 15.3 | 5.9 | 0.08 | 1.1 | <0.02 | 0.3 | <0.015 | 0.02 | 8 | 0.17 | 2 | - | 1 | 1 | 2020-06-15 | - | 4 | - | 9 | 2020-06-15 | 3 | 0.15 | - | 8 | 0.33 | - | 1 | 0.02 | 760
2019-07-08 | 2 | 192931 | 3 | 15.8 | 5.6 | 0.22 | 0.7 | 0.09 | 5.2 |  | 0.65 | 16 | 0.69 | 5 | - | 19 | 17
2019-08-21 | 2 | 193601 | 3.2 | 14.5 | 7.8 | 0.22 | 0.8 | 0.04 | 5.9 |  | 0.6 | 18 | 0.6 | 7 | -* | 2 | 2
2019-09-10 | 2 | 193883 | 3.14 | 14.1 | 5.9 | 0.18 | 0.5 | 0.03 | 3.5 |  | 0.6 | 14 | 0.65 | 5 | - | 1 | 1 | Note: Resample due to F/coli and Ecoli results on 7 April 2020 on bores 1, 2, 3, and Spring
2019-10-11 | 2 | 194340 | 2.92 | 13.6 | 5.9 | 0.17 | 0.5 | <0.02 | 3 |  | 0.62 | 13 | 0.62 | <1 | - | 2 | 2 | Note: Exceedance in Conditions 19 and 20, and breach of Conditions 20 and 21
2019-11-21 | 2 | 194974 | 2.95 | 13.1 | 6.2 | 0.18 | 0.3 | <0.02 | 3.6 |  | 0.61 | 14 | 0.57 | 5 | - | <1 | - | Note: Exceedance in limits stipulated in Condition 19 for Bores 1, 2, 3, 4, 5, 6, 7 and Spring under Condition 18
2019-12-04 | 2 | 195206 | 3.1 | 13.1 | 5.7 | 0.18 | 0.8 | <0.02 | 4.2 |  | 0.54 | 14 | 0.55 | 4 | - | 1 | 1
2020-01-24 | 2 | 200342 | 3.16 | 13.8 | 5.7 | 0.16 | 0.3 | 0.02 | 3.2 | <0.015 | 0.47 | 13 | 0.51 | 3 | - | 2 | 2
2020-02-18 | 2 | 200761 | 3.17 | 13.7 | 5.7 | 0.16 | 0.2 | 0.03 | 2.9 | <0.015 | 0.54 | 14 | 0.48 | 4 | - | 18 | 17
2020-03-12 | 2 | 201194 | 3.12 | 13.8 | 6 | 0.17 | 0.7 | 0.02 | 3.8 | <0.015 | 0.57 | 14 | 0.57 | 7 | - | 1 | 1 | Average readings of DRP during report period
2020-04-07 | 2 | 201532 | 3.2 | 14.7 | 6.1 | 0.16 | 0.4 | <0.02 | 0.2 | <0.015 | 0.66 | 14 | 0.52 | 3 | - | 175 | 160 | Bore 1 | 0.029167
2020-04-08 | 2 | 201555 | - | - | - | - | - | - | - | - | - | - | - | - | - | 4 | 4 | Bore 2 | 0.5775
2020-05-21 | 2 | 202073 | 3.5 | 14.9 | 5.9 | 0.15 | 0.5 | <0.02 | 2.6 | <0.015 | 0.58 | 12 | 0.56 | <1 | - | 1 | 1 | Bore 3 | 0.54167
2020-06-15 | 2 | 202425 | 3.1 | 15.1 | 5.8 | 0.2 | 0.7 | <0.02 | <0.2 | 0.015 | 0.49 | 18 | 0.5 | 8 | - | 1 | 1 | Bore 4 | 0.1975
2019-07-08 | 3 | 192932 | 3.2 | 13.3 | 6 | 0.15 | 0.3 | <0.02 | 2.7 |  | 0.52 | 12 | 0.54 | 5 | - | 10 | 9 | Bore 4a | 0.059167
2019-08-21 | 3 | 193602 | 3.2 | 11 | 6.1 | 0.18 | 6.8 | 0.04 | 4.1 |  | 0.55 | 16 | 0.53 | 2 | - | 45 | 41 | Bore 5 | 0.26833
2019-09-10 | 3 | 193884 | 3.18 | 10.7 | 6 | 0.12 | 4.1 | <0.02 | 1.3 |  | 0.46 | 11 | 0.47 | <1 | - | 5 | 4 | Bore 6 | 0.025833
2019-10-11 | 3 | 194341 | 2.91 | 10.4 | 6.1 | 0.18 | 0.9 | <0.02 | 2.4 |  | 0.54 | 17 | 0.51 | <1 | - | <1 | - | Bore 7 | 0.0225
2019-11-21 | 3 | 194975 | 2.9 | 11.2 | 5.9 | 0.16 | 0.4 | <0.02 | 4.7 |  | 0.46 | 13 | 0.47 | 6 | - | 31 | 22 | Spring | 0.016364
2019-12-04 | 3 | 195207 | 2.97 | 11.9 | 5.8 | 0.13 | 8.2 | <0.02 | 1.9 |  | 0.53 | 11 | 0.51 | <1 | - | 48 | 42
2020-01-24 | 3 | 200343 | 3.21 | 15.4 | 5.9 | 0.11 | 0.3 | <0.02 | 0.7 | <0.015 | 0.53 | 7 | 0.55 | 1 | - | 1 | 1
2020-02-18 | 3 | 200762 | 3.18 | 16.3 | 5.8 | 0.13 | 8.6 | 0.05 | 1.2 | <0.015 | 0.52 | 12 | 0.52 | 2 | - | 3 | 3
2020-03-12 | 3 | 201195 | 3.16 | 17.6 | 6.3 | 0.11 | 0.6 | 0.02 | 0.6 | <0.015 | 0.6 | 9 | 0.57 | 5 | - | 1 | 1
2020-04-07 | 3 | 201533 | 3.4 | 17.5 | 6.1 | 0.1 | 0.3 | <0.02 | 0.7 | <0.015 | 0.59 | 12 | 0.39 | 2 | - | 9 | 7
2020-04-08 | 3 | 201556 | - | - | - | - | - | - | - | - | - | - | - | - | - | 11 | 10
2020-05-21 | 3 | 202074 | 3.22 | 15 | 6.1 | 0.13 | 0.8 | 0.02 | 0.8 | <0.015 | 0.6 | 13 | 0.5 | <1 | - | 2 | 2
2020-06-15 | 3 | 202426 | 3.4 | 14 | 6.3 | 0.12 | 1 | <0.02 | 1.6 | <0.015 | 0.6 | 10 | 0.48 | 1 | - | <1 | -
2019-07-08 | 4 | 192933 | 3.4 | 15 | 5.8 | 0.12 | 0.3 | <0.02 | 2 |  | 0.2 | 9 | 0.19 | <1 | 2 | <1 | -
2019-08-21 | 4 | 193603 | 3.5 | 14.6 | 6.1 | 0.12 | 0.8 | <0.02 | 2.2 |  | 0.19 | 12 | 0.19 | 3 | 2 | <1 | - (<1)
2019-09-10 | 4 | 193885 | 3.1 | 14.6 | 6.1 | 0.11 | 0.3 | <0.02 | 1.4 |  | 0.18 | 10 | 0.18 | 2 | 1 | <1 | *
2019-10-11 | 4 | 194342 | 2.89 | 13.9 | 6 | 0.1 | 0.7 | <0.02 | 1.1 |  | 0.22 | 9 | 0.18 | <1 | <1 | <1 | -
2019-11-21 | 4 | 194976 | 3.4 | 13.5 | 5.9 | 0.13 | 0.5 | <0.02 | 2.4 |  | 0.18 | 9 | 0.18 | 6 | 2 | <1 | -
2019-12-04 | 4 | 195208 | 3 | 13.2 | 5.8 | 0.11 | 0.7 | <0.02 | 1.8 |  | 0.17 | 10 | 0.15 | 1 | <1 | <1 | *
2020-01-24 | 4 | 200344 | 3.11 | 13.3 | 5.8 | 0.09 | 0.2 | 0.03 | 0.7 | <0.015 | 0.17 | 7 | 0.21 | 2 | 3 | <1 | <1
2020-02-18 | 4 | 200763 | 3.2 | 13 | 5.7 | 0.09 | 0.2 | <0.02 | 0.7 | <0.015 | 0.17 | 8 | 0.17 | 6 | 3 | <1 | <1
2020-03-12 | 4 | 201196 | 2.42 | 13.2 | 6 | 0.1 | 0.6 | 0.02 | 1.1 | <0.015 | 0.18 | 9 | 0.16 | 1 | 3 | 3 | 3
2020-04-07 | 4 | 201534 | 3.4 | 13.6 | 6.1 | 0.09 | 0.1 | <0.02 | 0.8 | <0.015 | 0.2 | 9 | 0.17 | <1 | - | 1 | <1
2020-05-21 | 4 | 202075 | 3.73 | 14.1 | 5.9 | 0.1 | 0.9 | 0.02 | 1.3 | <0.015 | 0.36 | 9 | 0.17 | <1 | <1 | <1 | -
2020-06-15 | 4 | 202427 | 3.2 | 14.5 | 5.8 | 0.13 | 0.8 | <0.02 | 2.7 | <0.015 | 0.15 | 12 | 0.15 | 3 | 4 | <1 | -
2019-07-08 | 4a | 192934 | 3.4 | 14.8 | 5.6 | 0.09 | 0.3 | <0.02 | 0.1 |  | 0.07 | 8 | 0.08 | <1 | - | 10 | 10
2019-08-21 | 4a | 193604 | 3.4 | 14.4 | 6.3 | 0.09 | 1.1 | <0.02 | 0.9 |  | 0.06 | 11 | 0.08 | 1 | - | <1 | - (<1)
2019-09-10 | 4a | 193886 | 3.28 | 14.6 | 5.9 | 0.09 | 0.4 | <0.02 | 0.7 |  | 0.06 | 9 | 0.06 | 1 | - | <1 | *
2019-10-11 | 4a | 194343 | 3.12 | 14.2 | 6.5 | 0.09 | 1.2 | <0.02 | 0.6 |  | 0.07 | 9 | 0.05 | <1 | - | <1 | -
2019-11-21 | 4a | 194977 | 3.1 | 14.2 | 6.7 | 0.09 | 0.5 | <0.02 | 0.7 |  | 0.05 | 5 | 0.05 | 1 | - | 4 | 4
2019-12-04 | 4a | 195209 | 3.25 | 13.8 | 5.9 | 0.07 | 0.8 | <0.02 | 0.8 |  | 0.05 | 9 | 0.03 | <1 | - | <1 | *
2020-01-24 | 4a | 200345 | 3.25 | 13.9 | 6 | 0.09 | 0.4 | 0.03 | 0.6 | <0.015 | 0.06 | 6 | 0.1 | 3 | - | <1 | <1
2020-02-18 | 4a | 200764 | 3.04 | 13.8 | 6 | 0.09 | 0.3 | 0.02 | 0.7 | <0.015 | 0.07 | 9 | 0.06 | 1 | - | 2 | 2
2020-03-12 | 4a | 201197 | 3.55 | 13.3 | 6 | 0.09 | 0.5 | <0.02 | 0.7 | <0.015 | 0.06 | 7 | 0.06 | 1 | - | <1 | <1
2020-04-07 | 4a | 201535 | 3.6 | 13.6 | 6 | 0.09 | 0.2 | <0.02 | 0.5 | <0.015 | 0.05 | 9 | 0.05 | <1 | - | <1 | <1
2020-05-21 | 4a | 202076 | 4.15 | 14.2 | 6.1 | 0.09 | 0.7 | <0.02 | 0.5 | <0.015 | 0.05 | 8 | 0.08 | <1 | - | <1 | -
2020-06-15 | 4a | 202428 | 3.4 | 14.2 | 6 | 0.09 | 1.1 | <0.02 | 0.6 | <0.015 | 0.06 | 8 | 0.06 | 3 | - | 1 | 1
2019-07-08 | 5 | 192935 | 2.8 | 14.7 | 5.6 | 0.27 | 0.5 | <0.02 | 5.8 |  | 0.25 | 2 | 0.29 | 6 | 3 | <1 | -
2019-08-21 | 5 | 193605 | 2.98 | 13.6 | 6.3 | 0.3 | 1.1 | <0.02 | 9.8 |  | 0.23 | 21 | 0.25 | 10 | 9 | 5 | 5
2019-09-10 | 5 | 193887 | 2.89 | 13.3 | 5.9 | 0.25 | 0.6 | <0.02 | 5.4 |  | 0.3 | 18 | 0.35 | 9 | 8 | 5 | 4
2019-10-11 | 5 | 194344 | 2.66 | 13.3 | 5.9 | 0.27 | 0.7 | <0.02 | 0.6 |  | 0.04 | 22 | 0.26 | 4 | 6 | 2 | 2
2019-11-21 | 5 | 194978 | 3.1 | 14.4 | 5.9 | 0.23 | 0.7 | <0.02 | 3.2 |  | 0.25 | 15 | 0.3 | 5 | 2 | 2 | 1
2019-12-04 | 5 | 195210 | 2.65 | 14.8 | 5.6 | 0.28 | 0.9 | <0.02 | 5.2 |  | 0.25 | 23 | 0.25 | 4 | 1 | 1 | 1
2020-01-24 | 5 | 200346 | 2.9 | 16.3 | 5.7 | 0.26 | 0.5 | 0.02 | 2.4 | 0.029 | 0.31 | 18 | 0.35 | 5 | 5 | 3 | 3
2020-02-18 | 5 | 200765 | 2.94 | 16.5 | 5.7 | 0.24 | 0.4 | 0.02 | 0.7 | 0.021 | 0.3 | 20 | 0.31 | 6 | 2 | 230 | 159
2020-03-12 | 5 | 201198 | 2.8 | 17 | 5.9 | 0.28 | 1 | 0.02 | 4 | 0.03 | 0.31 | 25 | 0.31 | 7 | 7 | 6 | 6
2020-04-07 | 5 | 201536 | 3.1 | 16.8 | 5.9 | 0.25 | 0.4 | <0.02 | 2.9 | 0.019 | 0.3 | 21 | 0.33 | 3 | - | 3 | 1
2020-05-21 | 5 | 202077 | 3.75 | 15.6 | 6 | 0.2 | 0.8 | <0.02 | 2.3 | 0.031 | 0.35 | 17 | 0.43 | <1 | <1 | <1 | -
2020-06-15 | 5 | 202429 | 2.9 | 14.6 | 5.8 | 0.24 | 1.2 | <0.02 | 5.5 | 0.02 | 0.33 | 20 | 0.35 | 8 | 9 | <1 | -
2019-07-08 | 6 | 192936 | 3.3 | 13.1 | 6.3 | 0.07 | 0.6 | 0.02 | 0.3 |  | 0.03 | 8 | 0.03 | <1 | - | 9 | 6
2019-08-21 | 6 | 193606 | 3.5 | 11.2 | 6.4 | 0.08 | 1 | <0.02 | 0.4 |  | 0.04 | 10 | 0.03 | 1 | - | 2 | 2
2019-09-10 | 6 | 193888 | 3.88 | 10.6 | 6.7 | 0.07 | 0.5 | <0.02 | 0.3 |  | 0.02 | 7 | 0.06 | 1 | - | 2 | 2
2019-10-11 | 6 | 194345 | 2.62 | 10.4 | 6.5 | 0.07 | 0.5 | <0.02 | <0.2 |  | 0.02 | 7 | 0.02 | <1 | - | <1 | -
2019-11-21 | 6 | 194979 | 2.9 | 11.1 | 6.3 | 0.07 | 0.6 | <0.02 | <0.2 |  | 0.03 | 5 | 0.02 | <1 | - | 4 | 4
2019-12-04 | 6 | 195211 | 2.86 | 11.6 | 6.1 | 0.07 | 0.7 | <0.02 | 0.2 |  | 0.02 | 8 | <0.01 | <1 | - | 1 | 1
2020-01-24 | 6 | 200347 | 3.38 | 14.5 | 6 | 0.07 | 0.7 | 0.03 | <0.2 | <0.015 | 0.03 | 6 | 0.05 | 1 | - | <1 | <1
2020-02-18 | 6 | 200766 | 3.18 | 15.7 | 6 | 0.07 | 0.2 | 0.02 | <0.2 | <0.015 | 0.02 | 7 | 0.02 | 1 | - | 1 | <1
2020-03-12 | 6 | 201199 | 3.4 | 16.9 | 6.3 | 0.07 | 0.4 | <0.02 | <0.2 | <0.015 | 0.01 | 6 | 0.02 | 2 | - | <1 | <1
2020-04-07 | 6 | 201537 | 3.7 | 16.5 | 6.5 | 0.07 | 0.2 | <0.02 | <0.2 | <0.015 | 0.04 | 7 | 0.02 | <1 | - | <1 | <1
2020-05-21 | 6 | 202078 | 3.48 | 15.4 | 6.7 | 0.08 | 0.8 | <0.02 | <0.2 | <0.015 | 0.02 | 8 | 0.03 | <1 | - | 1 | 1
2020-06-15 | 6 | 202430 | 3.1 | 14 | 6.2 | 0.08 | 1 | <0.02 | 0.3 | <0.015 | 0.03 | 9 | 0.02 | <1 | - | 1 | <1
2019-07-08 | 7 | 192937 | 3.4 | 11.3 | 6.3 | 0.07 | 0.8 | <0.02 | <0.2 |  | 0.03 | 7 | 0.02 | <1 | - | 9 | 8
2019-08-21 | 7 | 193607 | 3.4 | 9.5 | 6.6 | 0.07 | 1.3 | <0.02 | <0.2 |  | 0.02 | 9 | 0.04 | 2 | - | <1 | - (<1)
2019-09-10 | 7 | 193889 | 3.56 | 9.4 | 6.6 | 0.07 | 2 | 0.02 | <0.2 |  | 0.02 | 8 | 0.03 | <1 | - | <1 | *
2019-10-11 | 7 | 194346 | 3.11 | 10.1 | 6.7 | 0.06 | 0.9 | <0.02 | <0.2 |  | 0.03 | 7 | 0.02 | <1 | - | <1 | -
2019-11-21 | 7 | 194980 | 4.3 | 12.3 | 6.2 | 0.07 | 0.5 | <0.02 | <0.2 |  | 0.02 | 3 | 0.01 | <1 | - | <1 | -
2019-12-04 | 7 | 195212 | 3.23 | 13.3 | 6.2 | 0.71 | 0.8 | <0.02 | 0.1 |  | 0.01 | 8 | 0.04 | <1 | - | 1 | 1
2020-01-24 | 7 | 200348 | 3.63 | 17.1 | 6.2 | 0.07 | 0.4 | 0.02 | <0.2 | <0.015 | 0.03 | 6 | 0.02 | <1 | - | 1 | 1
2020-02-18 | 7 | 200767 | 3.55 | 18.5 | 6.1 | 0.07 | 0.2 | <0.02 | <0.2 | <0.015 | 0.02 | 7 | 0.03 | 2 | - | <1 | <1
2020-03-12 | 7 | 201200 | 3.55 | 18.6 | 6.4 | 0.07 | 0.9 | 0.03 | <0.2 | <0.015 | 0.03 | 7 | 0.04 | 3 | - | <1 | <
2020-04-07 | 7 | 201538 | 3.4 | 17.1 | 6.5 | 0.07 | <0.1 | <0.02 | <0.2 | <0.015 | 0.02 | 8 | 0.01 | <1 | - | 2 | 1
2020-05-21 | 7 | 202079 | 3.7 | 13.1 | 6.6 | 0.07 | 0.6 | 0.02 | <0.2 | <0.015 | 0.02 | 8 | 0.03 | <1 | - | 4 | 4
2020-06-15 | 7 | 202431 | 3.9 | 11.1 | 6.5 | 0.07 | 1.3 | <0.02 | <0.2 | <0.015 | 0.02 | 8 | 0.02 | 4 | - | 2 | 2
2019-07-08 | Spring | 192938 | - | 13 | 6 | 0.09 | 1.5 | <0.02 | 0.7 |  | 0.03 | 7 | 0.02 | 1 | - | <1 | -
2019-08-21 | Spring | 193608 | - | 13.6 | 7.7 | 0.1 | 2.7 | <0.02 | 0.8 |  | 0.01 | 12 | 0.02 | <1 | - | <1 | -(<1)
2019-09-10 | Spring | 193890 | - | 11.1 | 6.3 | 0.1 | 2.9 | <0.02 | 0.6 |  | 0.01 | 8 | 0.03 | <1 | - | 660 | 380
2019-10-11 | Spring | 194347 | - | 14.2 | 6.1 | 0.09 | 5.3 | <0.02 | 0.7 |  | 0.01 | 9 | 0.04 | 1 | - | 13 | 11
2019-11-21 | Spring | 194981 | - | 15.1 | 6.4 | 0.09 | 1.9 | <0.02 | 0.6 |  | 0.02 | 5 | 0.02 | <1 | - | 111 | 110
2019-12-04 | Spring | 195213 | - | 16.3 | 6.1 | 0.92 | 2.9 | <0.02 | 0.5 |  | 0.01 | 9 | <0.01 | <1 | - | 3200 | 2900
2020-01-24 | Spring | 200349 | - | 9.3 | 6.1 | 0.09 | 3.4 | 0.02 | 0.5 | <0.015 | 0.03 | 6 | 0.27 | 2 | - | 900 | 490
2020-02-18 | Spring | 200768 | - | 17.9 | 6.4 | 0.08 | 5.8 | 0.02 | 0.3 | <0.015 | <0.01 | 7 | 0.03 | <1 | - | 600 | 840
2020-03-12 | Spring | 201201 | - | 16.6 | 6.3 | 0.08 | 4 | 0.03 | 0.3 | <0.015 | 0.01 | 7 | 0.05 | 2 | - | 580 | 510
2020-04-07 | Spring | 201539 | - | 14.8 | 7.1 | 0.08 | 6.4 | <0.02 | <0.2 | <0.015 | 0.01 | 8 | 0.05 | 2 | - | 5800 | 5600
2020-04-08 | Spring | 201557 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1300 | 1000
2020-05-21 | Spring | 202080 | - | 14.1 | 6.9 | 0.09 | 4.3 | <0.02 | 0.5 | <0.015 | 0.02 | 8 | 0.02 | <1 | - | 2 | 2
2020-06-15 | Spring | 202432 | - | 13.1 | 6.6 | 0.09 | 2.5 | <0.02 | 0.6 | <0.015 | 0.02 | 8 | 0.02 | 1 | - | 1000 | 760

## Condition21 Bore & Spring 2016+
SampleDate / Bore ID | DRP | TN | FColi | Ecoli | Average readings of DRP from Dec 2016 - Jun 2020
2016-11-10 |  |  |  |  | Bore 1 | 0.029512
Ot 1 |  |  | 2 | 5 | Bore 2 | 0.75927
Ot 2 |  |  | 1 | <5 | Bore 3 | 0.63098
Ot 3 |  |  | 8 | 135 | Bore 4 | 0.24098
Ot 4 |  |  | <1 | <1 | Bore 4a | 0.063415
Ot 4a |  |  | <1 | <1 | Bore 5 | 0.17195
Ot 5 |  |  | 1 | 5 | Bore 6 | 0.021707
2016-12-14 |  |  |  |  | Bore 7 | 0.021026
Ot 1 | 0.02 | <1 | 1 | 1
Ot 2 | 0.77 | 5 | <1 | -
Ot 3 | 0.48 | 2 | 6 | 5
Ot 4 | 0.24 | 4 | <1 | -
Ot 4a | 0.04 | 5 | <1 | -
Ot 5 | 0.12 | 11 | 3 | 3
Qt 6 | 0.01 | 1 | 1 | 1
Qt 7 | <0.01 | 2 | 1 | 1
Spring | <0.01 | 4 | 1 | 1
2017-01-06
Ot 1 | 0.02 | 2 | <1 | -
Ot 2 | 0.79 | 4 | 1 | 1
Ot 3 | 0.5 | 1 | 2 | 2
Ot 4 | 0.27 | 2 | <1 | -
Ot 4a | 0.06 | 7 | <1 | -
Ot 5 | 0.12 | 3 | <1 | -
Qt 6 | 0.02 | 2 | 1 | 1
Qt 7 | 0.01 | <1 | 1 | 1
Spring | 0.02 | 1 | <1 | -
2017-02-14
Ot 1 | 0.02 | <1 | <1 | -
Ot 2 | 0.73 | <1 | 1 | 1
Ot 3 | 0.47 | 2 | 26 | 20
Ot 4 | 0.29 | <1 | <1 | -
Ot 4a | 0.07 | 9 | <1 | -
Ot 5 | 0.12 | 3 | 2 | 2
Qt 6 | 0.02 | 10 | 3 | 2
Qt 7 | 0.02 | 3 | 1 | <1
Spring | 0.01 | 7 | <1 | -
2017-03-06
Ot 1 | 0.02 | 1 | 1 | <1
Ot 2 | 0.84 | 4 | <1 | -
Ot 3 | 0.54 | 1 | 7 | 5
Ot 4 | 0.27 | 2 | <1 | -
Ot 4a | 0.06 | 7 | <1 | -
Ot 5 | 0.12 | 5 | <1 | -
Qt 6 | 0.02 | 3 | 1 | 1
Qt 7 | 0.02 | 1 | <1 | -
Spring | 0.05 | 5 | <1 | -
2017-04-06
Ot 1 | 0.03 | <1 | 75 | 56
Ot 2 | 0.9 | 11 | <1 | -
Ot 3 | 0.56 | 1 | 9 | 8
Ot 4 | 0.29 | 3 | <1 | -
Ot 4a | 0.07 | <1 | <1 | -
Ot 5 | 0.11 | 3 | 2 | 2
Qt 6 | 0.02 | <1 | 3 | 3
Qt 7 | 0.03 | <1 | 1 | <1
Spring | 0.04 | <1 | 2 | 2
2017-05-10
Ot 1 | 0.05 | 3 | 5 | 3
Ot 2 | 0.83 | 11 | 1 | 1
Ot 3 | 0.52 | 5 | 12 | 10
Ot 4 | 0.25 | 13 | <1 | -
Ot 4a | 0.06 | 6 | <1 | -
Ot 5 | 0.13 | 5 | <1 | -
Qt 6 | 0.02 | 2 | <1 | -
Qt 7 | <0.01 | 7 | <1 | -
Spring | <0.01 | 2 | <1 | -
2017-06-02
Ot 1 | 0.04 | 5 | <1 | -
Ot 2 | 0.87 | 4 | 1 | <1
Ot 3 | 0.57 | 3 | 3 | 2
Ot 4 | 0.23 | <1 | <1 | -
Ot 4a | 0.06 | 1 | <1 | -
Ot 5 | 0.13 | 6 | 1 | 1
Qt 6 | 0.03 | 1 | <1 | -
Qt 7 | 0.02 | <1 | <1 | -
Spring | 0.04 | 5 | <1 | -
2017-08-14
Ot 1 | 0.02 | 1 | <1 | -
Ot 2 | 0.69 | 1 | 46 | 40
Ot 3 | 0.66 | 3 | 165 | 165
Ot 4 | 0.19 | 1 | <1 | -
Ot 4a | 0.06 | <1 | <1 | -
Ot 5 | 0.13 | 2 | <1 | -
Qt 6 | 0.03 | <1 | <1 | -
Qt 7 | 0.02 | <1 | <1 | -
Spring | 0.03 | <1 | 21 | 18
2017-09-14
Ot 1 | 0.02 | <1 | 1 | 1
Ot 2 | 0.68 | 1 | 1060 | 700
Ot 3 | 0.57 | 3 | 2 | 2
Ot 4 | 0.23 | 2 | 1 | 1
Ot 4a | 0.07 | 2 | <1 | -
Ot 5 | 0.16 | 1 | <1 | -
Qt 6 | 0.02 | <1 | <1 | -
Qt 7 | 0.01 | <1 | 1 | 1
Spring | <0.01 | 2 | 2 | 2
2017-10-18
Ot 1 | 0.04 | 3 | <1 | -
Ot 2 | 0.82 | 1 | 12 | 10
Ot 3 | 0.7 | 4 | 33 | 29
Ot 4 | 0.28 | <1 | 1 | 1
Ot 4a | 0.06 | <1 | <1 | -
Ot 5 | 0.13 | <1 | <1 | -
Qt 6 | 0.02 | <1 | 2 | 1
Qt 7 | 0.01 | <1 | <1 | -
Spring | 0.01 | <1 | 210 | 180
2017-11-15
Ot 1 | 0.03 | <1 | <1 | -
Ot 2 | 0.94 | 1 | 410 | 330
Ot 3 | 0.75 | <1 | 1 | <1
Ot 4 | 0.27 | <1 | <1 | -
Ot 4a | 0.07 | <1 | <1 | -
Ot 5 | 0.14 | <1 | <1 | -
Qt 6 | 0.02 | <1 | <1 | -
Qt 7 | 0.02 | <1 | 3 | 3
Spring | 0.02 | 3 | <2 | -
2017-12-12
Ot 1 | 0.03 | <1 | <1 | -
Ot 2 | 0.82 | 1 | 3 | 2
Ot 3 | 0.79 | <1 | 4 | 3
Ot 4 | 0.29 | 1 | <1 | -
Ot 4a | 0.07 | <1 | <1 | -
Ot 5 | 0.13 | <1 | <1 | -
Qt 6 | 0.02 | <1 | <1 | -
Qt 7 | 0.02 | <1 | <1 | -
Spring | 0.01 | <1 | 760 | 570
2018-01-19
Ot 1 | 0.02 | <1 | 1 | 1
Ot 2 | 0.8 | 3 | 27 | 23
Ot 3 | 0.65 | 3 | 230 | 200
Ot 4 | 0.24 | <1 | <1 | -
Ot 4a | 0.06 | <1 | <1 | -
Ot 5 | 0.13 | <1 | 1 | 1
Qt 6 | 0.02 | <1 | <1 | -
Qt 7 | 0.02 | <1 | <1 | -
Spring | 0.02 | 2 | 8 | 2
2018-02-19
Ot 1 | 0.03 | 9 | <1 | -
Ot 2 | 0.85 | 9 | 360 | 290
Ot 3 | 0.92 | 6 | 380 | 320
Ot 4 | 0.27 | 4 | <1 | -
Ot 4a | 0.07 | 13 | 1 | 1
Ot 5 | 0.13 | <1 | <1 | -
Qt 6 | 0.02 | 3 | 5 | 5
Qt 7 | 0.02 | 3 | <1 | -
Spring | 0.02 | 10 | 1700 | 1600
2018-03-14
Ot 1 | 0.04 | 16 | <1 | -
Ot 2 | 0.91 | 9 | 1990 | 1900
Ot 3 | 0.97 | 9 | 16 | 14
Ot 4 | 0.27 | 6 | <1 | -
Ot 4a | 0.07 | 7 | <1 | -
Ot 5 | 0.02 | 6 | 1 | 1
Qt 6 | 0.02 | 13 | 1 | 1
Qt 7 | 0.02 | 11 | <1 | -
Spring | 0.03 | 6 | 3 | 3
2018-03-28
SampleDate | ctlChloride | Text128 | ctlFColi | Text104
Ot 1 | - | - | - | -
Ot 2 | - | - | 20 | 10
Ot 3 | - | - | - | -
Ot 4 | - | - | - | -
Ot 4a | - | - | - | -
Ot 5 | - | - | - | -
Qt 6 | - | - | - | -
Qt 7 | - | - | - | -
Spring | - | - | - | -
2018-04-12
Ot 1 | 0.03 | <1 | 4 | 2
Ot 2 | 0.93 | <1 | 330 | 320
Ot 3 | 0.87 | <1 | 320 | 250
Ot 4 | 0.29 | 2 | 21 | 12
Ot 4a | 0.07 | <1 | 12 | 11
Ot 5 | 0.11 | 4 | 1 | 1
Qt 6 | 0.03 | <1 | 3 | 3
Qt 7 | 0.02 | <1 | 1 | 1
Spring | 0.03 | <1 | <2 | -
2018-05-15
Ot 1 | 0.03 | <1 | <1 | -
Ot 2 | 0.96 | 1 | 6 | 6
Ot 3 | 0.81 | 2 | 180 | 180
Ot 4 | 0.3 | 3 | <1 | -
Ot 4a | 0.07 | <1 | 1 | 1
Ot 5 | 0.13 | 7 | 7 | 6
Qt 6 | 0.02 | 3 | 1 | 1
Qt 7 | 0.02 | <1 | <1 | -
Spring | 0.02 | <1 | 102 | 88
2018-06-01
Ot 1 | 0.03 | <1 | <1 | -
Ot 2 | 0.78 | <1 | 490 | 360
Ot 3 | 0.69 | <1 | <2 | -
Ot 4 | 0.26 | <1 | 1 | 1
Ot 4a | 0.06 | <1 | 1 | 1
Ot 5 | 0.12 | <1 | 1 | 1
Qt 6 | 0.02 | <1 | 2 | 2
Qt 7 | 0.02 | <1 | <1 | -
Spring | 0.02 | <1 | <2 | -
2018-07-16
Ot 1 | 0.03 | 6 | <1 | -
Ot 2 | 0.77 | 3 | <1 | -
Ot 3 | 0.56 | 6 | 4 | 4
Ot 4 | 0.26 | 2 | <1 | -
Ot 4a | 0.08 | 5 | <1 | -
Ot 5 | 0.12 | <1 | 11 | 9
Qt 6 | 0.02 | <1 | 3 | 3
Qt 7 | 0.02 | <1 | <1 | -
Spring | 0.03 | <1 | 200 | 200
2018-08-28
Ot 1 | 0.03 | <1 | <1 | -
Ot 2 | 0.81 | <1 | 19 | 17
Ot 3 | 0.69 | 1 | 50 | 30
Ot 4 | 0.25 | <1 | <1 | -
Ot 4a | 0.07 | <1 | <1 | -
Ot 5 | 0.14 | <1 | <1 | -
Qt 6 | 0.02 | <1 | 2 | 2
Qt 7 | 0.02 | <1 | <1 | -
Spring | 0.02 | <1 | <1 | -
2018-09-19
Ot 1 | 0.03 | <1 | <1 | -
Ot 2 | 0.83 | 3 | 4 | 4
Ot 3 | 0.67 | 5 | 1 | <1
Ot 4 | 0.26 | 3 | <1 | -
Ot 4a | 0.06 | 1 | <1 | -
Ot 5 | 0.14 | 1 | <1 | -
Qt 6 | 0.02 | 2 | <1 | -
Qt 7 | 0.02 | 5 | <1 | -
Spring | 0.01 | 7 | 880 | 780
2018-10-25
Ot 1 | 0.04 | 4 | <1 | -
Ot 2 | 0.79 | 9 | 7 | 7
Ot 3 | 0.51 | 3 | 4 | 4
Ot 4 | 0.24 | 7 | <1 | -
Ot 4a | 0.06 | <1 | <1 | -
Ot 5 | 0.14 | 3 | <1 | -
Qt 6 | 0.02 | 4 | <1 | -
Qt 7 | 0.02 | 3 | <1 | -
Spring | 0.02 | <1 | 500 | 450
2018-11-19
Ot 1 | 0.04 | <1 | <1 | -
Ot 2 | 0.83 | <1 | <1 | -
Ot 3 | 0.6 | <1 | 1 | 1
Ot 4 | 0.26 | 3 | <1 | -
Ot 4a | 0.07 | <1 | <1 | -
Ot 5 | 0.13 | 2 | <1 | -
Qt 6 | 0.02 | 1 | <1 | -
Qt 7 | 0.02 | 1 | <1 | -
Spring | 0.02 | 8 | 38 | 34
2018-12-11
Ot 1 | 0.03 | <1 | <1 | -
Ot 2 | 0.85 | <1 | 11 | 8
Ot 3 | 0.65 | <1 | 5 | 4
Ot 4 | 0.25 | <1 | <1 | -
Ot 4a | 0.07 | <1 | <1 | -
Ot 5 | 0.14 | <1 | <1 | -
Qt 6 | 0.02 | <1 | <1 | -
Qt 7 | 0.03 | <1 | <1 | -
Spring | 0.02 | <1 | <1 | 440
2019-01-25
Ot 1 | 0.04 | <1 | 1 | 1
Ot 2 | 0.88 | <1 | 1 | 1
Ot 3 | 0.8 | 1 | 1 | 1
Ot 4 | 0.25 | <1 | <1 | -
Ot 4a | 0.06 | 2 | <1 | -
Ot 5 | 0.05 | 1 | 9 | 1
Qt 6 | 0.03 | <1 | 1 | 1
Qt 7 | 0.04 | <1 | <1 | -
Spring | 0.03 | 2 | 190 | 190
2019-02-18
Ot 1 | 0.03 | <1 | <1 | -
Ot 2 | 0.81 | <1 | 13 | 7
Ot 3 | 0.82 | <1 | 2 | 1
Ot 4 | 0.23 | <1 | <1 | -
Ot 4a | 0.06 | <1 | <1 | -
Ot 5 | 0.17 | <1 | <1 | -
Qt 6 | 0.02 | <1 | 1 | 1
Qt 7 | 0.02 | <1 | <1 | -
Spring | 0.03 | <1 | 61 | 50
2019-03-20
Ot 1 | 0.03 | <1 | <1 | -
Ot 2 | 0.87 | <1 | <1 | -
Ot 3 | 0.75 | <1 | 2 | 2
Ot 4 | 0.26 | <1 | <1 | -
Ot 4a | 0.06 | <1 | <1 | -
Ot 5 | 0.18 | <1 | 17 | 13
Qt 6 | 0.01 | <1 | 2 | 2
Qt 7 | 0.02 | <1 | <1 | -
Spring | 0.02 | <1 | 2900 | 2300
2019-04-09
Ot 1 | 0.02 | <1 | 1 | 1
Ot 2 | 0.9 | <1 | <1 | -
Ot 3 | 0.75 | <1 | 1 | 1
Ot 4 | 0.23 | <1 | <1 | -
Ot 4a | 0.07 | <1 | <1 | -
Ot 5 | 0.22 | <1 | 13 | 10
Qt 6 | 0.02 | <1 | 1 | 1
Qt 7 | 0.02 | <1 | <1 | -
Spring | 0.02 | <1 | <1 | -
2019-05-31
Ot 1 | 0.01 | 3 | <1 | -
Ot 2 | 0.71 | 5 | 2 | 2
Ot 3 | 0.58 | 6 | 1 | 1
Ot 4 | 0.22 | 4 | <1 | -
Ot 4a | 0.05 | 3 | <1 | -
Ot 5 | 0.25 | 3 | 2 | 1
Qt 6 | 0.01 | 5 | 1 | 1
Qt 7 | 0.01 | 1 | <1 | -
Spring | <0.01 | 1 | <2 | -
2019-06-13
Ot 1 | 0.03 | <1 | 6 | 5
Ot 2 | 0.73 | 4 | 8 | 6
Ot 3 | 0.57 | 5 | 12 | 10
Ot 4 | 0.22 | 3 | 2 | 2
Ot 4a | 0.09 | 2 | 1 | 1
Ot 5 | 0.3 | 14 | 2 | 2
Qt 6 | 0.02 | <1 | 1 | 1
Qt 7 | 0.03 | 2 | 2 | 2
Spring | 0.03 | <1 | <2 | <2
2019-07-08
Ot 1 | 0.02 | <1 | <1 | -
Ot 2 | 0.65 | 5 | 19 | 17
Ot 3 | 0.52 | 5 | 10 | 9
Ot 4 | 0.2 | <1 | <1 | -
Ot 4a | 0.07 | <1 | 10 | 10
Ot 5 | 0.25 | 6 | <1 | -
Qt 6 | 0.03 | <1 | 9 | 6
Qt 7 | 0.03 | <1 | 9 | 8
Spring | 0.03 | 1 | <1 | -
2019-08-21
Ot 1 | 0.03 | 4 | 3 | 2
Ot 2 | 0.6 | 7 | 2 | 2
Ot 3 | 0.55 | 2 | 45 | 41
Ot 4 | 0.19 | 3 | <1 | - (<1)
Ot 4a | 0.06 | 1 | <1 | - (<1)
Ot 5 | 0.23 | 10 | 5 | 5
Qt 6 | 0.04 | 1 | 2 | 2
Qt 7 | 0.02 | 2 | <1 | - (<1)
Spring | 0.01 | <1 | <1 | -(<1)
2019-09-10
Ot 1 | 0.02 | <1 | 2 | 1
Ot 2 | 0.6 | 5 | 1 | 1
Ot 3 | 0.46 | <1 | 5 | 4
Ot 4 | 0.18 | 2 | <1 | *
Ot 4a | 0.06 | 1 | <1 | *
Ot 5 | 0.3 | 9 | 5 | 4
Qt 6 | 0.02 | 1 | 2 | 2
Qt 7 | 0.02 | <1 | <1 | *
Spring | 0.01 | <1 | 660 | 380
2019-10-11
Ot 1 | 0.01 | <1 | <1 | -
Ot 2 | 0.62 | <1 | 2 | 2
Ot 3 | 0.54 | <1 | <1 | -
Ot 4 | 0.22 | <1 | <1 | -
Ot 4a | 0.07 | <1 | <1 | -
Ot 5 | 0.04 | 4 | 2 | 2
Qt 6 | 0.02 | <1 | <1 | -
Qt 7 | 0.03 | <1 | <1 | -
Spring | 0.01 | 1 | 13 | 11
2019-11-21
Ot 1 | 0.09 | <1 | <1 | -
Ot 2 | 0.61 | 5 | <1 | -
Ot 3 | 0.46 | 6 | 31 | 22
Ot 4 | 0.18 | 6 | <1 | -
Ot 4a | 0.05 | 1 | 4 | 4
Ot 5 | 0.25 | 5 | 2 | 1
Qt 6 | 0.03 | <1 | 4 | 4
Qt 7 | 0.02 | <1 | <1 | -
Spring | 0.02 | <1 | 111 | 110
2019-12-04
Ot 1 | 0.02 | <1 | 1 | 1
Ot 2 | 0.54 | 4 | 1 | 1
Ot 3 | 0.53 | <1 | 48 | 42
Ot 4 | 0.17 | 1 | <1 | *
Ot 4a | 0.05 | <1 | <1 | *
Ot 5 | 0.25 | 4 | 1 | 1
Qt 6 | 0.02 | <1 | 1 | 1
Qt 7 | 0.01 | <1 | 1 | 1
Spring | 0.01 | <1 | 3200 | 2900
2020-01-24
Ot 1 | 0.03 | 1 | 7 | 3
Ot 2 | 0.47 | 3 | 2 | 2
Ot 3 | 0.53 | 1 | 1 | 1
Ot 4 | 0.17 | 2 | <1 | <1
Ot 4a | 0.06 | 3 | <1 | <1
Ot 5 | 0.31 | 5 | 3 | 3
Qt 6 | 0.03 | 1 | <1 | <1
Qt 7 | 0.03 | <1 | 1 | 1
Spring | 0.03 | 2 | 900 | 490
2020-02-18
Ot 1 | 0.03 | <1 | 1 | 1
Ot 2 | 0.54 | 4 | 18 | 17
Ot 3 | 0.52 | 2 | 3 | 3
Ot 4 | 0.17 | 6 | <1 | <1
Ot 4a | 0.07 | 1 | 2 | 2
Ot 5 | 0.3 | 6 | 230 | 159
Qt 6 | 0.02 | 1 | 1 | <1
Qt 7 | 0.02 | 2 | <1 | <1
Spring | <0.01 | <1 | 600 | 840
2020-03-12
Ot 1 | 0.02 | 1 | <1 | <1
Ot 2 | 0.57 | 7 | 1 | 1
Ot 3 | 0.6 | 5 | 1 | 1
Ot 4 | 0.18 | 1 | 3 | 3
Ot 4a | 0.06 | 1 | <1 | <1
Ot 5 | 0.31 | 7 | 6 | 6
Qt 6 | 0.01 | 2 | <1 | <1
Qt 7 | 0.03 | 3 | <1 | <
Spring | 0.01 | 2 | 580 | 510
2020-04-07
Ot 1 | 0.04 | 1 | 60 | 49
Ot 2 | 0.66 | 3 | 175 | 160
Ot 3 | 0.59 | 2 | 9 | 7
Ot 4 | 0.2 | <1 | 1 | <1
Ot 4a | 0.05 | <1 | <1 | <1
Ot 5 | 0.3 | 3 | 3 | 1
Qt 6 | 0.04 | <1 | <1 | <1
Qt 7 | 0.02 | <1 | 2 | 1
Spring | 0.01 | 2 | 5800 | 5600
2020-04-08
Ot 1 | - | - | 4 | 2
Ot 2 | - | - | 4 | 4
Ot 3 | - | - | 11 | 10
Ot 4 | - | - | - | -
Ot 4a | - | - | - | -
Ot 5 | - | - | - | -
Qt 6 | - | - | - | -
Qt 7 | - | - | - | -
Spring | - | - | 1300 | 1000
2020-05-21
Ot 1 | 0.02 | <1 | 1 | 1
Ot 2 | 0.58 | <1 | 1 | 1
Ot 3 | 0.6 | <1 | 2 | 2
Ot 4 | 0.36 | <1 | <1 | -
Ot 4a | 0.05 | <1 | <1 | -
Ot 5 | 0.35 | <1 | <1 | -
Qt 6 | 0.02 | <1 | 1 | 1
Qt 7 | 0.02 | <1 | 4 | 4
Spring | 0.02 | <1 | 2 | 2
2020-06-15
Ot 1 | 0.02 | 2 | 1 | 1
Ot 2 | 0.49 | 8 | 1 | 1
Ot 3 | 0.6 | 1 | <1 | -
Ot 4 | 0.15 | 3 | <1 | -
Ot 4a | 0.06 | 3 | 1 | 1
Ot 5 | 0.33 | 8 | <1 | -
Qt 6 | 0.03 | <1 | 1 | <1
Qt 7 | 0.02 | 4 | 2 | 2
Spring | 0.02 | 1 | 1000 | 760